## Directions
Directions For use:
1. This spreadsheet was written using Microsoft Excel 97
2. Do not use preceding Y, X, C, etc... for PLC registers. Just use the register/coil number
3. Only the RED numbers should be changed
4. For the sheet to work correctly, enable: Tools >> Add Ins >> Analysis Toolpak (should be checked)

## Sheet2
Coils
REMEMBER, NO EIGHTS OR NINES!!! | Koyo PLC | Modbus |  |  |  | Modbus | Koyo PLC
Global Outputs GY0 - GY3777 | 0 | 1 |  |  | Coil 1 - 2048 | 1 | 0 | Global Outputs - GY
Outputs - Y0 - Y1777 | 0 | 2049 |  |  | Coil 2049 - 3072 | 2049 | 0 | Outputs - Y
Control Relay - C0 - C3777 | 0 | 3073 |  |  | Coil 3073 - 5120 | 3073 | 0 | Control Relay - C
Stage - S0 - S1777 | 0 | 5121 |  |  | Coil 5121 - 6144 | 5121 | 0 | Stage - S
Timer - T0 - T377 | 0 | 6145 |  |  | Coil 6145 - 6400 | 6145 | 0 | Timer - T
Counter - CT0 - CT377 | 0 | 6401 |  |  | Coil 6401 - 6656 | 6401 | 0 | Counter - CT
Inputs
Global Inputs GX0 - GX3777 | 0 | 10001 |  |  | Inputs 10001 - 12048 | 10001 | 0 | Global Inputs - GX
Inputs X0 - X1777 | 0 | 12049 |  |  | Inputs 12049 - 13072 | 12049 | 0 | Inputs - X
Special Register SP0 - SP777 | 0 | 13073 |  |  | Inputs 13073 - 13584 | 13073 | 0 | Special Register - SP
Registers
| PLC | Holding Registers | Input Registers |  |  | Modbus | V Memory
V Memory | 0 | 40001 | 30001 |  | Holding Registers | 40001 | 0
[5 empty] | Input Registers | 30001 | 0
Only the RED numbers should be changed.
Please refer to the "Function Code 4" sheet for information on RX and WX to the 30001 (Input Registers) with our PLCs.

## 340 Modbus
| 340 PLC | Modbus Hex | Modbus Decimal | Modbus Coil Decimal | Modbus Decimal | 340 PLC
Physical I/O 0 - 167 | 0 | 0 | 0 | 0 - 119 | 0 | 0
Control Relays 170 - 377 | 377 | FF | 255 | 120 - 255 | 120 | 170
Shift Register Bits 400 - 577 | 400 | 100 | 256 | 256 - 383 | 256 | 400
Timer/Counter Status 600 - 677 | 600 | 180 | 384 | 384 - 447 | 384 | 600
Physical IO 700 - 777 | 700 | 1C0 | 448 | 448 - 511 | 448 | 700
Control Relays 1000 - 1077 | 1077 | 23F | 575 | 512 - 575 | 512 | 1000
User Registers 400 - 577 | 400 | 40 | 64 | 64 - 127 | 64 | 400
Timer/Counter Acc. 600 - 677 | 600 | 0 | 0 | 0 - 63 | 0 | 600
User Registers 700 - 777 | 700 | 80 | 128 | 128 - 191 | 128 | 700

## Function code 4
NOTE: This is not necessary when using the MRX or MWX instructions. The MRX and MWX instructions allow you to specify the function code you want to use.
NOTE: H2-ECOM100, H0-ECOM100, and H4-ECOM100 modules will also support Function 4 over ethernet. The modules must have firmware versions equal to or greater than those listed below to support this. The feature is used by requesting EVEN numbers of bytes for 40001+ addresses (function code 3) and ODD numbers of bytes for 30001+ addresses (function code 4).
H0-ECOM100 = 4.0.52
H2-ECOM100 = 4.0.999
H4-ECOM100 = 4.0.1049