## GS20 Quick REF
GS20 PARAMETER SUMMARY |  |  |  | GS2 EquivalentPARAMETER SUMMARY |  | GS4 Equivalent PARAMETER SUMMARY |  | SORT ODER BY ANY DRIVE TYPE | SEE DISCLAIMER
GS20 Seq | GS20 Parameter Group | GS20 Pr.No. | GS20 Parameter Description | GS2 Pr. No. | GS2 Parameter Description | GS4 Pr. No. | GS4 Parameter Description
1 | P00 Drive | P00.00 | GS20 Model ID- Identity Code | P9.42 | Manufacturer Model Information | P09.42 | GS Model ID
2 | P00 Drive | P00.01 | Rated Current |  |  | P09.33 | GS4 Drive Rated Amps
3 | P00 Drive | P00.02 | Restore to Default | P9.07 P9.08 | Parameter Lock Restore to Default | P09.07 P09.08 | Parameter Lock Restore to Default
4 | P00 Drive | P00.03 | Start-up display Selection |  |  | P08.01 | Start-up Display Selection
5 | P00 Drive | P00.04 | User Display | P8.00 | User Defined Display Function | P08.00 | User Display
6 | P00 Drive | P00.05 | Coefficient Gain in Actual Output Frequency Display (H Page scale) | P8.01 | Frequency Scale Factor | P08.05 | Output Frequency Gain
7 | P00 Drive | P00.06 | Firmware version | P9.39 | Firmware Version | P09.39 | Firmware version
8 | P00 Drive | P00.07 | Parameter protection password input |  |  | P08.06 | Password Input
9 | P00 Drive | P00.08 | Parameter protection password setting |  |  | P08.07 | Password Set Up
10 | P00 Drive | P00.10 | Control Method- Torq or Speed
11 | P00 Drive | P00.11 | Speed (Velocity) Control mode | P2.00 | Volts/Hertz Settings | P02.11 | Control Mode
12 | P00 Drive | P00.16 | Torque duty selection |  |  | P06.34 | Variable/Constant Torque Duty Selection
13 | P00 Drive | P00.17 | Carrier frequency | P2.08 | PWM Carrier Frequency | P02.10 | PWM Carrier Frequency
14 | P00 Drive | P00.19 | PLC command mask |  |  | P09.34 | PLC Command Mask (status only)
15 | P00 Drive | P00.20 | Master frequency command source (AUTO, REMOTE) | P4.00 | Source of Frequency Command | P04.00 | 1st Source of Frequency Command [Remote]
16 | P00 Drive | P00.21 | Operation command source (AUTO, REMOTE) | P3.00 | Source of Operation Command | P03.00 | 1st Source of Operation Command [Remote]
17 | P00 Drive | P00.22 | Stop method | P1.00 | Stop Methods | P01.00 | Stop Method
18 | P00 Drive | P00.23 | Motor direction control | P6.03 | Reverse Operation Inhibit | P06.09 | Fwd/Rev Direction Inhibit
19 | P00 Drive | P00.24 | Digital operator (keypad) frequency command memory
20 | P00 Drive | P00.25 | User-defined characteristics (COEFF ATT) |  |  | P08.02 | User Defined Format
21 | P00 Drive | P00.26 | User-defined maximum value (COEFF MAX) | P7.01 | PV 100% Value | P08.03 | User Defined Max
22 | P00 Drive | P00.27 | User-defined value (COEFF SET) |  |  | P08.04 | User Defined Setpoint
23 | P00 Drive | P00.29 | LOCAL / REMOTE selection |  |  | P03.58 | Local/Remote Switch Mode
24 | P00 Drive | P00.30 | Master frequency command source (HAND, LOCAL) | P4.00 | Source of Frequency Command | P04.01 | 2nd Source of Frequency Command [Local]
25 | P00 Drive | P00.31 | Operation command source (HAND, LOCAL) | P3.00 | Source of Operation Command | P03.01 | 2nd Source of Operation Command [Local]
26 | P00 Drive | P00.32 | Digital keypad STOP function | P3.00 | Source of Operation Command
27 | P00 Drive | P00.35 | Auxiliary frequency source
28 | P00 Drive | P00.36 | Master and auxiliary frequency command selection
29 | P00 Drive | P00.48 | Display filter time (current)
30 | P00 Drive | P00.49 | Display filter time (keypad)
31 | P00 Drive | P00.50 | Date Code of Software version (date)
32 | P01 Basic | P01.00 | Maximum operation frequency | P0.04 | Motor Maximum RPM | P0.04 | Drive Maximum Output Frequency
33 | P01 Basic | P01.01 | Motor 1 Fbase | P0.02 | Motor Base Frequency | P0.02 | Motor 1 Base Frequency
34 | P01 Basic | P01.02 | Motor 1, Rated Voltage (Nameplate) | P0.00 | Motor Nameplate Voltage | P0.00 | Motor 1 Maximum Output Voltage
35 | P01 Basic | P01.03 | Motor 1, Mid-point frequency 1 | P2.04 | Mid-point Frequency | P02.04 | Motor 1 Middle Output Frequency 1
36 | P01 Basic | P01.04 | Motor 1, Mid-point voltage 1 | P2.05 | Mid-point Voltage | P02.05 | Motor 1 Middle Output Voltage 1
37 | P01 Basic | P01.05 | Motor 1, Mid-point frequency 2 |  |  | P02.06 | Motor 1 Middle Output Frequency 2
38 | P01 Basic | P01.06 | Motor 1, Mid-point voltage 2 |  |  | P02.07 | Motor 1 Middle Output Voltage 2
39 | P01 Basic | P01.07 | Motor 1, Minimum output frequency | P2.06 | Min. Output Frequency | P02.08 | Motor 1 Minimum Output Frequency
40 | P01 Basic | P01.08 | Motor 1, Minimum output voltage | P2.07 | Min. Output Voltage | P02.09 | Motor 1 Minimum Output Voltage
41 | P01 Basic | P01.09 | Start-up frequency |  |  | P02.19 | Start Frequency
42 | P01 Basic | P01.10 | Output frequency upper limit | P6.15 | Upper Bound of Output Frequency | P06.25 | Upper Limit of Output Frequency
43 | P01 Basic | P01.11 | Output frequency lower limit | P6.16 | Lower Bound of Output Frequency | P06.26 | Lower Limit of Output Frequency
44 | P01 Basic | P01.12 | Acceleration time 1 | P1.01 | Acceleration Time 1 | P01.01 | Acceleration Time 1
45 | P01 Basic | P01.13 | Deceleration time 1 | P1.02 | Deceleration Time 1 | P01.02 | Deceleration Time 1
46 | P01 Basic | P01.14 | Acceleration time 2 | P1.05 | Acceleration Time 2 | P01.03 | Acceleration Time 2
47 | P01 Basic | P01.15 | Deceleration time 2 | P1.06 | Deceleration Time 2 | P01.04 | Deceleration Time 2
48 | P01 Basic | P01.16 | Acceleration time 3 |  |  | P01.05 | Acceleration Time 3
49 | P01 Basic | P01.17 | Deceleration time 3 |  |  | P01.06 | Deceleration Time 3
50 | P01 Basic | P01.18 | Acceleration time 4 | P1.08 | Accel 1 to Accel 2 frequency transition | P01.07 | Acceleration Time 4
51 | P01 Basic | P01.19 | Deceleration time 4 | P1.08 | Accel 1 to Accel 2 frequency transition | P01.08 | Deceleration Time 4
52 | P01 Basic | P01.20 | JOG acceleration time |  |  | P01.13 | Jog Acceleration Time
53 | P01 Basic | P01.21 | JOG deceleration time |  |  | P01.14 | Jog Deceleration Time
54 | P01 Basic | P01.22 | JOG frequency | P5.00 | Jog | P05.00 | Jog Frequency
55 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | P1.08 P1.09 | Accel 1 to Accel 2 frequency transition Decel 2 to Decel 1 frequency transition. | P01.16 P01.17 P01.18 | Accel/Decel Transition Method Accel Trans Freq Decel Trans Freq
56 | P01 Basic | P01.24 | S-curve for acceleration begin time 1 | P1.03 | Accel S-curve | P01.09 | S-curve Accel Time 1
57 | P01 Basic | P01.25 | S-curve for acceleration arrival time 2 | P1.03 | Accel S-curve | P01.11 | S-curve Accel Time 2
58 | P01 Basic | P01.26 | S-curve for deceleration begin time 1 | P1.04 | Decel S-curve | P01.10 | S-curve Decel Time 1
59 | P01 Basic | P01.27 | S-curve for deceleration arrival time 2 | P1.04 | Decel S-curve | P01.12 | S-curve Decel Time 2
60 | P01 Basic | P01.28 | Skip frequency 1 (upper limit) | P1.10 | Skip Frequency 1 | P01.19 | Skip Frequency 1 Upper Limit
61 | P01 Basic | P01.29 | Skip frequency 1 (lower limit) | P1.10 | Skip Frequency 1 | P01.20 | Skip Frequency 1 Lower Limit
62 | P01 Basic | P01.30 | Skip frequency 2 (upper limit) | P1.11 | Skip Frequency 2 | P01.21 | Skip Frequency 2 Upper Limit
63 | P01 Basic | P01.31 | Skip frequency 2 (lower limit) | P1.11 | Skip Frequency 2 | P01.22 | Skip Frequency 2 Lower Limit
64 | P01 Basic | P01.32 | Skip frequency 3 (upper limit) | P1.12 | Skip Frequency 3 | P01.23 | Skip Frequency 3 Upper Limit
65 | P01 Basic | P01.33 | Skip frequency 3 (lower limit) | P1.12 | Skip Frequency 3 | P01.24 | Skip Frequency 3 Lower Limit
66 | P01 Basic | P01.34 | Zero-speed mode |  |  | P02.18 | Zero Speed Select
67 | P01 Basic | P01.35 | Motor 2, Output frequency (Base frequency / Motor's rated frequency) |  |  | P0.13 | Motor 2 Base Frequency
68 | P01 Basic | P01.36 | Motor 2, Output voltage (Base voltage / Motor's rated voltage) |  |  | P0.11 | Motor 2 Maximum Output Voltage
69 | P01 Basic | P01.37 | Motor 2, Mid-point frequency |  |  | P02.12 | Motor 2 Middle Output Frequency 1
70 | P01 Basic | P01.38 | Motor 2, Mid-point voltage 1 |  |  | P02.13 | Motor 2 Middle Output Voltage 1
71 | P01 Basic | P01.39 | Motor 2, Mid-point frequency 2 |  |  | P02.14 | Motor 2 Middle Output Frequency 2
72 | P01 Basic | P01.40 | Motor 2, Mid-point voltage 2 |  |  | P02.15 | Motor 2 Middle Output Voltage 2
73 | P01 Basic | P01.41 | Motor 2, Minimum output frequency |  |  | P02.16 | Motor 2 Minimum Output Frequency
74 | P01 Basic | P01.42 | Motor 2, Minimum output voltage |  |  | P02.17 | Motor 2 Minimum Output Voltage
75 | P01 Basic | P01.43 | V/F curve selection | P2.00 | Volts/Hertz Settings | P02.00 | Volts/Hertz Settings
76 | P01 Basic | P01.44 | Auto-acceleration and auto-deceleration setting | P6.06 | Auto Adjustable Accel/Decel | P06.13 | Auto Adjustable Accel/ Decel
77 | P01 Basic | P01.45 | Time unit for accel/decel and S-curve |  |  | P01.15 | Time Unit for Accel/Decel & S-curve
78 | P01 Basic | P01.49 | Regenerative energy restriction control (decel method) |  |  | P01.29 | Deceleration Method
79 | P01 Basic | P01.52 | Motor 2, Maximum operation frequency
80 | P01 Basic | P01.53 | Motor 3, Maximum operation frequency
81 | P01 Basic | P01.54 | Motor 3, Output frequency (Base frequency / Motor's rated frequency)
82 | P01 Basic | P01.55 | Motor 3, Output voltage (Base voltage / Motor's rated voltage)
83 | P01 Basic | P01.56 | Motor 3, Mid-point frequency 1
84 | P01 Basic | P01.57 | Motor 3, Mid-point voltage 1
85 | P01 Basic | P01.58 | Motor 3, Mid-point frequency 2
86 | P01 Basic | P01.59 | Motor 3, Mid-point voltage 2
87 | P01 Basic | P01.60 | Motor 3, Minimum output frequency
88 | P01 Basic | P01.61 | Motor 3, Minimum output voltage
89 | P01 Basic | P01.62 | Motor 4, Maximum operation frequency
90 | P01 Basic | P01.63 | Motor 4, Output frequency (Base frequency / Motor's rated frequency)
91 | P01 Basic | P01.64 | Motor 4, Output voltage (Base voltage / Motor's rated voltage)
92 | P01 Basic | P01.65 | Motor 4, Mid-point frequency 1
93 | P01 Basic | P01.66 | Motor 4, Mid-point voltage 1
94 | P01 Basic | P01.67 | Motor 4, Mid-point frequency 2
95 | P01 Basic | P01.68 | Motor 4, Mid-point voltage 2
96 | P01 Basic | P01.69 | Motor 4, Minimum output frequency
97 | P01 Basic | P01.70 | Motor 4, Minimum output voltage
98 | P02 Digital IO | P02.00 | Two-wire / three- wire operation control | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P03.02 | 2/3 Wire Operation Mode
99 | P02 Digital IO | P02.01 | Multi-function input command 1 (FWD/DI1) | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P03.03 | Multi-Function Input (DI1)
100 | P02 Digital IO | P02.02 | Multi-function input command 2 (REV/DI2) | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P03.04 | Multi-Function Input (DI2)
101 | P02 Digital IO | P02.03 | Multi-function input command 3 (DI3) | P3.02 | Multi-function Input (DI3) | P03.05 | Multi-Function Input (DI3)
102 | P02 Digital IO | P02.04 | Multi-function input command 4 (DI4) | P3.03 | Multi-function Input (DI4) | P03.06 | Multi-Function Input (DI4)
103 | P02 Digital IO | P02.05 | Multi-function input command 5 (DI5) | P3.04 | Multi-function Input (DI5) | P03.07 | Multi-Function Input (DI5)
104 | P02 Digital IO | P02.06 | Multi-function input command 6 (DI6) | P3.05 | Multi-function Input (DI6) | P03.08 | Multi-Function Input (DI6)
105 | P02 Digital IO | P02.07 | Multi-function input command 7 (DI7) |  |  | P03.09 | Multi-Function Input (DI7)
106 | P02 Digital IO | P02.09 | UP / DOWN key mode |  |  | P03.39 | Increase/Decrease Speed Mode
107 | P02 Digital IO | P02.10 | Constant speed, accel/decele speed of UP/DOWN Key |  |  | P03.40 | DI6 Counter Debounce Filter
108 | P02 Digital IO | P02.11 | Multi-function input response time |  |  | P03.41 | Digital Input Response Time
109 | P02 Digital IO | P02.12 | Multi-function input mode selection |  |  | P03.42 | Multi-Function Input Contact Selection (0=N.O. / 1=N.C.)
110 | P02 Digital IO | P02.13 | Multi-function output 1 (R1) | P3.11 | Multi-Function Output Terminal 1 | P03.17 | Multi-Function Output Terminal 1 (Relay 1 or PLC Y0)
111 | P02 Digital IO | P02.16 | Multi-function output 2 (DO1) | P3.12 | Multi-Function Output Terminal 2 | P03.19 | Multi-Function Output Terminal 3 (DO1 or PLC Y3)
112 | P02 Digital IO | P02.17 | Multi-function output 3 (DO2) |  |  | P03.20 | Multi-Function Output Terminal 4 (DO2 or PLC Y4)
113 | P02 Digital IO | P02.18 | Multi-function output direction ACT |  |  | P03.43 | Multi-Function Output Contact Selection (0=N.O. / 1=N.C.)
114 | P02 Digital IO | P02.19 | Terminal counting value reached (returns to 0) |  |  | P03.44 | Final Counter Value
115 | P02 Digital IO | P02.20 | Preliminary (Middle) counting value reached (does not return to 0) |  |  | P03.45 | Mid-point Counter Value
116 | P02 Digital IO | P02.21 | Digital output gain (DO) |  |  | P03.38 | Frequency Output (FO) Scaling Factor
117 | P02 Digital IO | P02.22 | Desired frequency reached 1 | P3.16 | Desired Frequency | P03.32 | Desired Frequency 1
118 | P02 Digital IO | P02.23 | The bandwidth of the desired frequency reached 1 |  |  | P03.33 | Desired Frequency 1 Width
119 | P02 Digital IO | P02.24 | Desired frequency reached 2 |  |  | P03.34 | Desired Frequency 2
120 | P02 Digital IO | P02.25 | bandwidth of desired freq reached 2 |  |  | P03.35 | Desired Frequency 2 Width
121 | P02 Digital IO | P02.34 | Output frequency setting for digital output terminal |  |  | P03.53 | Output Frequency Threshold for Multi- Function Output Terminals
122 | P02 Digital IO | P02.35 | External operation control selection after fault reset and reboot | P6.30 | Line Start Lockout | P06.29 | Line Start Lockout
123 | P02 Digital IO | P02.47 | Motor RPM zero- speed level
124 | P02 Digital IO | P02.50 | Display the status of multi-function input terminals DI1-DI7 |  |  | P03.46 | Digital Input Active Status
125 | P02 Digital IO | P02.51 | Display the status of multi-function output terminals R1, DO1, DO2 |  |  | P03.47 | Digital Output Active Status
126 | P02 Digital IO | P02.52 | Display the external multi-function input terminals DI1-DI7 used by PLC |  |  | P03.48 | PLC – Digital Input Mask
127 | P02 Digital IO | P02.53 | Display the external multi-function output terminals R1, DO1, DO2 used by PLC |  |  | P03.49 | PLC – Digital Output Mask
128 | P02 Digital IO | P02.54 | Display the frequency command executed by external terminal (EXT Speed REC) |  |  | P03.50 | Increase/Decrease Speed Command Record
129 | P02 Digital IO | P02.58 | Multi-function output terminal (function 42): brake frequency check point
130 | P02 Digital IO | P02.78 | Motor deceleration gear ratio
131 | P02 Digital IO | P02.79 | Automatic index positioning angle setting
132 | P02 Digital IO | P02.80 | Automatic index positioning deceleration time
133 | P02 Digital IO | P02.81 | EF activates when the terminal count value reached
134 | P02 Digital IO | P02.82 | Initial Frequency com-mand (F) mode after stop
135 | P02 Digital IO | P02.83 | Initial Frequency com-mand (F) setting after stop
136 | P03 Analog IO | P03.00 | Analog input selection (AI1) |  |  | P04.02 | Analog Input 1 (AI1) Function
137 | P03 Analog IO | P03.01 | Analog input selection (AI2) | P4.00 | Source of Frequency Command | P04.03 | Analog Input 2 (AI2) Function
138 | P03 Analog IO | P03.03 | Analog input bias (AI1) |  |  | P04.10 | AI1 Input Bias (Offset)
139 | P03 Analog IO | P03.04 | Analog input bias (AI2) | P4.02 | Analog Input Offset | P04.15 | AI2 Input Bias (Offset)
140 | P03 Analog IO | P03.07 | Positive / negative bias mode (AI1) |  |  | P04.11 | AI1 Input Bias (Offset) Polarity
141 | P03 Analog IO | P03.08 | Positive / negative bias mode (AI2) | P4.01 | Analog Input Offset Polarity | P04.16 | AI2 Input Bias (Offset) Polarity
142 | P03 Analog IO | P03.10 | Reverse setting when analog signal input is negative frequency | P4.04 | Analog Input Reverse Motion Enable | P04.09 | Analog Frequency Command for Reverse Run
143 | P03 Analog IO | P03.11 | Analog input gain (AI1) |  |  | P04.12 | AI1 Input Gain
144 | P03 Analog IO | P03.12 | Analog input gain (AI2) | P4.03 | Analog Input Gain | P04.17 | AI2 Input Gain
145 | P03 Analog IO | P03.15 | Analog input filter (LPF) time (AI1) |  |  | P04.13 | AI1 Filter
146 | P03 Analog IO | P03.16 | Analog input filter (LPF) time (AI2) |  |  | P04.18 | AI2 Filter
147 | P03 Analog IO | P03.18 | Analog input addition function
148 | P03 Analog IO | P03.19 | Signal loss selection for analog input 4-20 mA | P4.05 | Loss of ACI Signal (4-20mA) | P04.64 | Loss of AI2 Signal (4~20mA)
149 | P03 Analog IO | P03.20 | Multi-function output (A01) | P4.11 | Analog Output Signal | P04.50 | Analog Output 1 (AO1)
150 | P03 Analog IO | P03.21 | Analog output gain (A01) | P4.12 | Analog Output Gain | P04.51 | AO1 Gain
151 | P03 Analog IO | P03.22 | Analog output in REV direction (A01) |  |  | P04.52 | AO1 Negative Value Handle
152 | P03 Analog IO | P03.27 | A01 output bias
153 | P03 Analog IO | P03.28 | AI1 terminal input selection |  |  | P04.05 | AI1 – I/V Selection
154 | P03 Analog IO | P03.29 | AI2 terminal input selection |  |  | P04.06 | AI2 – I/V Selection
155 | P03 Analog IO | P03.30 | PLC analog output terminal status |  |  | P04.62 | PLC Analog Output Mask
156 | P03 Analog IO | P03.31 | A01 output selection |  |  | P04.53 | AO1 0~20mA/4~20mA Selection
157 | P03 Analog IO | P03.32 | A01 DC output setting level |  |  | P04.60 | AO1 Output Constant Level
158 | P03 Analog IO | P03.35 | A01 output filter time
159 | P03 Analog IO | P03.39 | VR (keypad dial) input selection
160 | P03 Analog IO | P03.40 | VR (keypad dial) input bias
161 | P03 Analog IO | P03.41 | VR (keypad dial) positive / negative bias
162 | P03 Analog IO | P03.42 | VR (keypad dial) gain
163 | P03 Analog IO | P03.43 | VR (keypad dial) filter time
164 | P03 Analog IO | P03.44 | Multi-function output (DO) by AI level source
165 | P03 Analog IO | P03.45 | AI upper level
166 | P03 Analog IO | P03.46 | AI lower level
167 | P03 Analog IO | P03.50 | Analog input curve calculation selection |  |  | P04.24 | AI V/Hz Calculated Selection
168 | P03 Analog IO | P03.57 | AI2 lowest point |  |  | P04.31 | AI2 Low V/A
169 | P03 Analog IO | P03.58 | AI2 proportional lowest point |  |  | P04.32 | AI2 Low Hz Percent
170 | P03 Analog IO | P03.59 | AI2 mid-point |  |  | P04.33 | AI2 Mid V/A
171 | P03 Analog IO | P03.60 | AI2 proportional mid- point |  |  | P04.34 | AI2 Mid Hz Percent
172 | P03 Analog IO | P03.61 | AI2 highest point |  |  | P04.35 | AI2 High V/A
173 | P03 Analog IO | P03.62 | AI2 proportional highest point |  |  | P04.36 | AI2 High Hz Percent
174 | P03 Analog IO | P03.63 | AI1 voltage lowest point |  |  | P04.25 | AI1 Low V/A
175 | P03 Analog IO | P03.64 | AI1 proportional lowest point |  |  | P04.26 | AI1 Low Hz Percent
176 | P03 Analog IO | P03.65 | AI1 voltage mid-point |  |  | P04.27 | AI1 Mid V/A
177 | P03 Analog IO | P03.66 | AI1 proportional mid- point |  |  | P04.28 | AI1 Mid Hz Percent
178 | P03 Analog IO | P03.67 | AI1 voltage highest point |  |  | P04.29 | AI1 High V/A
179 | P03 Analog IO | P03.68 | AI1 proportional highest point |  |  | P04.30 | AI1 High Hz Percent
180 | P03 Analog IO | P03.69 | Negative AI1 voltage highest point |  |  | P04.43 | -AI3 High Voltage Bipolar
181 | P03 Analog IO | P03.70 | Negative AI1 proportional highest point |  |  | P04.44 | -AI3 High Hz Percent Bipolar
182 | P03 Analog IO | P03.71 | Negative AI1 voltage mid-point |  |  | P04.45 | -AI3 Mid Voltage Bipolar
183 | P03 Analog IO | P03.72 | Negative AI1 proportional mid-point |  |  | P04.46 | -AI3 Mid Hz Percent Bipolar
184 | P03 Analog IO | P03.73 | Negative AI1 voltage lowest point |  |  | P04.47 | -AI3 Low Voltage Bipolar
185 | P03 Analog IO | P03.74 | Negative AI1 proportional lowest point |  |  | P04.48 | -AI3 Low Hz Percent Bipolar
186 | P04 Multi Step Spd | P04.00 | 1st step speed frequency | P5.01 | Multi-Speed 1 | P05.01 | Multi-Speed 1
187 | P04 Multi Step Spd | P04.01 | 2nd step speed frequency | P5.02 | Multi-Speed 2 | P05.02 | Multi-Speed 2
188 | P04 Multi Step Spd | P04.02 | 3rd step speed frequency | P5.03 | Multi-Speed 3 | P05.03 | Multi-Speed 3
189 | P04 Multi Step Spd | P04.03 | 4th step speed frequency | P5.04 | Multi-Speed 4 | P05.04 | Multi-Speed 4
190 | P04 Multi Step Spd | P04.04 | 5th step speed frequency | P5.05 | Multi-Speed 5 | P05.05 | Multi-Speed 5
191 | P04 Multi Step Spd | P04.05 | 6th step speed frequency | P5.06 | Multi-Speed 6 | P05.06 | Multi-Speed 6
192 | P04 Multi Step Spd | P04.06 | 7th step speed frequency | P5.07 | Multi-Speed 7 | P05.07 | Multi-Speed 7
193 | P04 Multi Step Spd | P04.07 | 8th step speed frequency |  |  | P05.08 | Multi-Speed 8
194 | P04 Multi Step Spd | P04.08 | 9th step speed frequency |  |  | P05.09 | Multi-Speed 9
195 | P04 Multi Step Spd | P04.09 | 10th step speed frequency |  |  | P05.10 | Multi-Speed 10
196 | P04 Multi Step Spd | P04.10 | 11th step speed frequency |  |  | P05.11 | Multi-Speed 11
197 | P04 Multi Step Spd | P04.11 | 12th step speed frequency |  |  | P05.12 | Multi-Speed 12
198 | P04 Multi Step Spd | P04.12 | 13th step speed frequency |  |  | P05.13 | Multi-Speed 13
199 | P04 Multi Step Spd | P04.13 | 14th step speed frequency |  |  | P05.14 | Multi-Speed 14
200 | P04 Multi Step Spd | P04.14 | 15th step speed frequency |  |  | P05.15 | Multi-Speed 15
201 | P04 Multi Step Spd | P04.50 | PLC buffer 0 |  |  | P08.20 | PLC Buffer 1
202 | P04 Multi Step Spd | P04.51 | PLC buffer 1 |  |  | P08.21 | PLC Buffer 2
203 | P04 Multi Step Spd | P04.52 | PLC buffer 2 |  |  | P08.22 | PLC Buffer 3
204 | P04 Multi Step Spd | P04.53 | PLC buffer 3 |  |  | P08.23 | PLC Buffer 4
205 | P04 Multi Step Spd | P04.54 | PLC buffer 4 |  |  | P08.24 | PLC Buffer 5
206 | P04 Multi Step Spd | P04.55 | PLC buffer 5 |  |  | P08.25 | PLC Buffer 6
207 | P04 Multi Step Spd | P04.56 | PLC buffer 6 |  |  | P08.26 | PLC Buffer 7
208 | P04 Multi Step Spd | P04.57 | PLC buffer 7 |  |  | P08.27 | PLC Buffer 8
209 | P04 Multi Step Spd | P04.58 | PLC buffer 8 |  |  | P08.28 | PLC Buffer 9
210 | P04 Multi Step Spd | P04.59 | PLC buffer 9 |  |  | P08.29 | PLC Buffer 10
211 | P04 Multi Step Spd | P04.60 | PLC buffer 10 |  |  | P08.30 | PLC Buffer 11
212 | P04 Multi Step Spd | P04.61 | PLC buffer 11 |  |  | P08.31 | PLC Buffer 12
213 | P04 Multi Step Spd | P04.62 | PLC buffer 12 |  |  | P08.32 | PLC Buffer 13
214 | P04 Multi Step Spd | P04.63 | PLC buffer 13 |  |  | P08.33 | PLC Buffer 14
215 | P04 Multi Step Spd | P04.64 | PLC buffer 14 |  |  | P08.34 | PLC Buffer 15
216 | P04 Multi Step Spd | P04.65 | PLC buffer 15 |  |  | P08.35 | PLC Buffer 16
217 | P04 Multi Step Spd | P04.66 | PLC buffer 16 |  |  | P08.36 | PLC Buffer 17
218 | P04 Multi Step Spd | P04.67 | PLC buffer 17 |  |  | P08.37 | PLC Buffer 18
219 | P04 Multi Step Spd | P04.68 | PLC buffer 18 |  |  | P08.38 | PLC Buffer 19
220 | P04 Multi Step Spd | P04.69 | PLC buffer 19 |  |  | P08.39 | PLC Buffer 20
221 | P05 Motor | P05.00 | Motor parameter auto-tuning |  |  | P0.05 | Motor Auto Tune
222 | P05 Motor | P05.01 | Induction Motor 1, Full-load amps | P0.01 | Motor Nameplate Amps | P0.01 | Motor 1 Rated Current
223 | P05 Motor | P05.02 | Induction Motor 1, Rated power (kW) |  |  | P0.08 | Motor 1 Rated Horsepower (HP)
224 | P05 Motor | P05.03 | Induction Motor 1, Rated speed (rpm) | P0.03 | Motor Base RPM | P0.03 | Motor 1 Rated RPM
225 | P05 Motor | P05.04 | Induction Motor 1, Number of poles |  |  | P0.09 | Motor 1 Number of Poles
226 | P05 Motor | P05.05 | Induction Motor 1, No-load amps |  |  | P0.07 | Motor 1 No-Load Current
227 | P05 Motor | P05.06 | Induction Motor 1, Stator resistance (Rs) |  |  | P0.06 | Motor 1 Resistance
228 | P05 Motor | P05.07 | Induction Motor 1, Rotor resistance (Rr)
229 | P05 Motor | P05.08 | Induction Motor 1, Magnetizing inductance (Lm)
230 | P05 Motor | P05.09 | Induction Motor 1, Stator inductance (Lx)
231 | P05 Motor | P05.13 | Induction Motor 2, Full-load amps |  |  | P0.12 | Motor 2 Rated Current
232 | P05 Motor | P05.14 | Induction Motor 2, Rated power (kW) |  |  | P0.17 | Motor 2 Rated Horsepower (HP)
233 | P05 Motor | P05.15 | Induction Motor 2, Rated speed (rpm) |  |  | P0.14 | Motor 2 Rated RPM
234 | P05 Motor | P05.16 | Induction Motor 2, Number of poles |  |  | P0.18 | Motor 2 Number of Poles
235 | P05 Motor | P05.17 | Induction Motor 2, No- load amps |  |  | P0.16 | Motor 2 No-Load Current
236 | P05 Motor | P05.18 | Induction Motor 2, Stator resistance (Rs) |  |  | P0.15 | Motor 2 Resistance
237 | P05 Motor | P05.19 | Induction Motor 2, Rotor resistance (Rr)
238 | P05 Motor | P05.20 | Induction Motor 2, Magnetizing inductance (Lm)
239 | P05 Motor | P05.21 | Induction Motor 2, Stator inductance (Lx)
240 | P05 Motor | P05.22 | Multi-motor (induction) selection |  |  | P0.10 | Motor 1 or 2 Selection
241 | P05 Motor | P05.23 | Frequency for Y-connection / fl-connection switch for an induction motor |  |  | P02.20 | Y-D Switching Frequency
242 | P05 Motor | P05.24 | Y-connection /fl-con switch for an ind motor |  |  | P02.21 | Y-D Switching Enable
243 | P05 Motor | P05.25 | Delay time for Y-connection /fl-connection switch for an induction motor |  |  | P02.22 | Delay Time for Y-D Switching
244 | P05 Motor | P05.26 | Accumulated Watt- second for a motor in low word (W-msec.)
245 | P05 Motor | P05.27 | Accumulated Watt- second for a motor in high word (W-sec.)
246 | P05 Motor | P05.28 | Accumulated Watt- hour for a motor (W-hour)
247 | P05 Motor | P05.29 | Accumulated Watt- hour for a motor in low word (kW-hour)
248 | P05 Motor | P05.30 | Accumulated Watt- hour for a motor in high word (MW-hour)
249 | P05 Motor | P05.31 | Accumulated motor operation time (Minutes) |  |  | P08.11 | Accumulative Motor Operation Time (minute)
250 | P05 Motor | P05.32 | Accumulated motor operation time (days) |  |  | P08.12 | Accumulative Motor Operation Time (day)
251 | P05 Motor | P05.33 | Induction motor (IM) or permanent magnet synchronous AC motor (PM) selection
252 | P05 Motor | P05.34 | Full-load current for a permanent magnet synchronous AC motor
253 | P05 Motor | P05.35 | Rated power for a permanent magnet synchronous AC motor
254 | P05 Motor | P05.36 | Rated speed for a permanent magnet synchronous AC motor
255 | P05 Motor | P05.37 | Number of poles for a permanent magnet synchronous AC motor
256 | P05 Motor | P05.39 | Stator resistance Rs for a permanent magnet synchronous AC motor
257 | P05 Motor | P05.40 | Permanent magnet synchronous AC motor Ld
258 | P05 Motor | P05.41 | Permanent magnet synchronous AC motor Lq
259 | P05 Motor | P05.43 | Ke parameter of a permanent magnet synchronous AC motor
260 | P05 Motor | P05.64 | Induction Motor 3, Full-load amps
261 | P05 Motor | P05.65 | Induction Motor 3, Rated power (kW)
262 | P05 Motor | P05.66 | Induction Motor 3, Rated speed (rpm)
263 | P05 Motor | P05.67 | Induction Motor 3, Number of poles
264 | P05 Motor | P05.68 | Induction Motor 3, No- load amps
265 | P05 Motor | P05.69 | Induction Motor 3, Stator resistance (Rs)
266 | P05 Motor | P05.70 | Induction Motor 4, Full-load amps
267 | P05 Motor | P05.71 | Induction Motor 4, Rated power for (kW)
268 | P05 Motor | P05.72 | Induction Motor 4, Rated speed (rpm)
269 | P05 Motor | P05.73 | Induction Motor 4, Number of poles
270 | P05 Motor | P05.74 | Induction Motor 4, No-load amps
271 | P05 Motor | P05.75 | Induction Motor 4, Stator resistance (Rs)
272 | P06 Protection | P06.00 | Low voltage level |  |  | P06.35 | Low Voltage Level
273 | P06 Protection | P06.01 | Over-voltage stall prevention | P6.05 | Over-Voltage Stall Prevention | P06.11 P06.27 | Over-Voltage Stall Prevention Over-Voltage Stall Prev Level
274 | P06 Protection | P06.02 | Selection for over-voltage stall prevention |  |  | P06.12 | Selection for Over- voltage Stall Prevention
275 | P06 Protection | P06.03 | Over-current stall prevention during acceleration (OCA) | P6.10 | Over-Current Stall Prevention during Acceleration | P06.20 | Over-Current Stall Prevention Level During Accel
276 | P06 Protection | P06.04 | Over-current stall prevention during operation (OCN) | P6.11 | Over-Current Stall Prevention during Operation | P06.21 | Over-Current Stall Prevention Level During Operation
277 | P06 Protection | P06.05 | Acceleration / deceleration time selection for stall prevention at constant speed |  |  | P06.36 | OC Stall Preventation Accel/Decel Time Selection at Normal Speed
278 | P06 Protection | P06.06 | Over-torque detection selection (motor 1) | P6.07 | Over-Torque Detection Mode | P06.14 | Over-Torque Detection Mode (OT1)
279 | P06 Protection | P06.07 | Over-torque detection level (motor 1) | P6.08 | Over-Torque Detection Level | P06.15 | Over-Torque Detection Level (OT1)
280 | P06 Protection | P06.08 | Over-torque detection time (motor 1) | P6.09 | Over-Torque Detection Time | P06.16 | Over-Torque Detection Time (OT1)
281 | P06 Protection | P06.09 | Over-torque detection selection (motor 2) |  |  | P06.17 | Over-Torque Detection Mode (OT2)
282 | P06 Protection | P06.10 | Over-torque detection level (motor 2) |  |  | P06.18 | Over-Torque Detection Level (OT2)
283 | P06 Protection | P06.11 | Over-torque detection time (motor 2) |  |  | P06.19 | Over-Torque Detection Time (OT2)
284 | P06 Protection | P06.12 | Current limit |  |  | P06.38 | Torque Limit (Current Limit)
285 | P06 Protection | P06.13 | Electronic thermal relay selection 1 (motor 1) | P6.00 | Electronic Thermal Overload Relay | P06.00 | Electronic Thermal Overload Relay (Motor 1) NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS.
286 | P06 Protection | P06.14 | Electronic thermal relay action time 1 (motor 1) |  |  | P06.01 | Electronic Thermal Characteristic (Motor 1)
287 | P06 Protection | P06.15 | Temperature level overheat (OH) warning |  |  | P06.30 | Heat Sink OH Warning Level
288 | P06 Protection | P06.16 | Stall prevention limit level (Weak magnetic field current stall prevention level) |  |  | P06.37 | OC Stall Preventation Limit for operation over Rated Speed
289 | P06 Protection | P06.17 | Fault record 1 | P6.31 | Present Fault Record | P11.04 | First Fault Record
290 | P06 Protection | P06.18 | Fault record 2 | P6.32 | Second Most Recent Fault Record | P11.05 | Second Most Recent Fault Record
291 | P06 Protection | P06.19 | Fault record 3 | P6.33 | Third Most Recent Fault Record | P11.06 | Third Most Recent Fault Record
292 | P06 Protection | P06.20 | Fault record 4 | P6.34 | Fourth Most Recent Fault Record | P11.07 | Fourth Most Recent Fault Record
293 | P06 Protection | P06.21 | Fault record 5 | P6.35 | Fifth Most Recent Fault Record | P11.08 | Fifth Most Recent Fault Record
294 | P06 Protection | P06.22 | Fault record 6 | P6.36 | Sixth Most Recent Fault Record | P11.09 | Sixth Most Recent Fault Record
295 | P06 Protection | P06.23 | Fault output option 1 |  |  | P11.00 | Fault Output Option 1
296 | P06 Protection | P06.24 | Fault output option 2 |  |  | P11.01 | Fault Output Option 2
297 | P06 Protection | P06.25 | Fault output option 3 |  |  | P11.02 | Fault Output Option 3
298 | P06 Protection | P06.26 | Fault output option 4 |  |  | P11.03 | Fault Output Option 4
299 | P06 Protection | P06.27 | Electronic thermal relay selection 2 (motor 2) |  |  | P06.02 | Electronic Thermal Overload Relay (Motor 2) NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS.
300 | P06 Protection | P06.28 | Electronic thermal relay action time 2 (motor 2) |  |  | P06.03 | Electronic Thermal Characteristic (Motor 2)
301 | P06 Protection | P06.29 | PTC detection selection |  |  | P06.39 | PTC/RTD Detection Selection
302 | P06 Protection | P06.30 | PTC level |  |  | P06.40 | PTC Level
303 | P06 Protection | P06.31 | Frequency command at malfunction |  |  | P11.18 | Frequency Command at Fault
304 | P06 Protection | P06.32 | Output frequency at malfunction |  |  | P11.19 | Output Frequency at Fault
305 | P06 Protection | P06.33 | Output voltage at malfunction |  |  | P11.20 | Output Voltage at Fault
306 | P06 Protection | P06.34 | DC bus voltage at malfunction |  |  | P11.21 | DC Bus Voltage at Fault
307 | P06 Protection | P06.35 | Output current at malfunction |  |  | P11.22 | Output Current at Fault
308 | P06 Protection | P06.36 | IGBT temperature at malfunction |  |  | P11.23 | IGBT Temperature at Fault
309 | P06 Protection | P06.38 | Motor speed at malfunction |  |  | P11.25 | RPM of Motor at Fault
310 | P06 Protection | P06.39 | Torque command at malfunction
311 | P06 Protection | P06.40 | Status of the digital input terminal at malfunction |  |  | P11.26 | Digital Input Status at Fault
312 | P06 Protection | P06.41 | Status of the digital output terminal at malfunction |  |  | P11.27 | Digital Output Status at Fault
313 | P06 Protection | P06.42 | Drive status at malfunction |  |  | P11.28 | Drive Status at Fault
314 | P06 Protection | P06.44 | STO latch selection |  |  | P06.71 | STO Alarm Latch
315 | P06 Protection | P06.45 | Output phase loss detection action (OPHL) |  |  | P06.45 | Output Phase Loss (OPhL) Detection Selection
316 | P06 Protection | P06.46 | Detection time for output phase loss |  |  | P06.46 P06.69 | Output Phase Loss Detection time Input Phase Loss Detection Time
317 | P06 Protection | P06.47 | Current detection level for output phase loss |  |  | P06.47 P06.70 | Output Phase Loss Current Detection Level Input Phase Loss Ripple Detection
318 | P06 Protection | P06.48 | DC brake time for output phase loss |  |  | P03.51 P06.48 | Brake Delay Time Output Phase Loss DCI Time
319 | P06 Protection | P06.49 | LvX auto-reset
320 | P06 Protection | P06.53 | Input phase loss detection action (OrP) |  |  | P06.49 | Input Phase Loss Treatment
321 | P06 Protection | P06.55 | Derating protection |  |  | P06.33 | Drive Derating Method NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS.
322 | P06 Protection | P06.56 | PT100 voltage level 1 |  |  | P06.41 | RTD (PT100) Level 1, PTC Level Detection Selection
323 | P06 Protection | P06.57 | PT100 voltage level 2 |  |  | P06.42 | RTD (PT100) Level 2, PTC Level Detection Selection
324 | P06 Protection | P06.58 | PT100 level 1 frequency protection |  |  | P06.43 | RTD (PT100) Drop Frequency for PT100 Level 1
325 | P06 Protection | P06.59 | PT100 activation level 1 protection frequency delay time |  |  | P06.44 | RTD (PT100) Treatment Delay Time
326 | P06 Protection | P06.60 | Software detection GFF current level |  |  | P06.50 | GFF Detect Current Level (% of INV I-Rated)
327 | P06 Protection | P06.61 | Software detection GFF filter time |  |  | P06.51 | GFF Low Pass Filter Gain
328 | P06 Protection | P06.63 | Operation time of fault record 1 (Days) |  |  | P11.10 | Operating Time of Present Fault Record (Day)
329 | P06 Protection | P06.64 | Operation time of fault record 1 (Minutes) |  |  | P11.11 | Operating Time of Present Fault Record (Minute)
330 | P06 Protection | P06.65 | Operation time of fault record 2 (Days) |  |  | P11.12 | Operating Time of Second Most Recent Fault Record (Day)
331 | P06 Protection | P06.66 | Operation time of fault record 2 (Minutes) |  |  | P11.13 | Operating Time of Second Most Recent Fault Record (Minute)
332 | P06 Protection | P06.67 | Operation time of fault record 3 (Days) |  |  | P11.14 | Operating Time of Third Most Recent Fault Record (Day)
333 | P06 Protection | P06.68 | Operation time of fault record 3 (Minutes) |  |  | P11.15 | Operating Time of Third Most Recent Fault Record (Minute)
334 | P06 Protection | P06.69 | Operation time of fault record 4 (Days) |  |  | P11.16 | Operating Time of Fourth Most Recent Fault Record (Day)
335 | P06 Protection | P06.70 | Operation time of fault record 4 (Minutes) |  |  | P11.17 | Operating Time of Fourth Most Recent Fault Record (Minute)
336 | P06 Protection | P06.71 | Low current setting level |  |  | P06.52 | Low Current Level
337 | P06 Protection | P06.72 | Low current detection time |  |  | P06.53 | Low Current Detection Time
338 | P06 Protection | P06.73 | Low current action |  |  | P06.54 | Low Current Action
339 | P06 Protection | P06.80 | Fire mode |  |  | P06.55 | Fire Mode
340 | P06 Protection | P06.81 | Operating frequency in fire mode |  |  | P06.56 | Fire Mode Operation Frequency
341 | P06 Protection | P06.88 | Operation times in fire mode
342 | P06 Protection | P06.90 | Operation time of fault record 5 (days)
343 | P06 Protection | P06.91 | Operation time of fault record 5 (Minutes)
344 | P06 Protection | P06.92 | Operation time of fault record 6 (days)
345 | P06 Protection | P06.93 | Operation time of fault record 6 (Minutes)
346 | P07 Special | P07.00 | Software brake chopper threshold level |  |  | P06.28 | Dynamic Braking Voltage Level
347 | P07 Special | P07.01 | DC brake current level | P1.18 | DC Injection Current Level | P01.25 | DC Injection Current Level
348 | P07 Special | P07.02 | DC brake time at start-up | P1.20 | DC Injection during Start-up | P01.26 | DC Injection Time During Start-up
349 | P07 Special | P07.03 | DC brake time at STOP | P1.21 | DC Injection during Stopping | P01.27 | DC Injection Time During Stopping
350 | P07 Special | P07.04 | DC brake frequency at STOP | P1.22 | Start-point for DC Injection | P01.28 | Start-Point for DC Injection During Stopping
351 | P07 Special | P07.05 | Voltage increasing gain
352 | P07 Special | P07.06 | Restart after momentary power loss | P6.02 | Momentary Power Loss | P06.08 | Momentary Power Loss
353 | P07 Special | P07.07 | Allowed power loss duration | P6.12 | Maximum Allowable Power Loss Time | P06.22 | Maximum Allowable Power Loss Time
354 | P07 Special | P07.08 | Base Block time | P6.13 | Base-Block Time for Speed Search | P06.23 | Base-Block Time for Speed Search
355 | P07 Special | P07.09 | Current limit of speed tracking | P6.14 | Maximum Speed Search Current Level | P06.24 | Maximum Speed Search Current Level
356 | P07 Special | P07.10 | Restart after fault action |  |  | P06.06 | Base Block Speed Search after Fault (oc,ov,bb)
357 | P07 Special | P07.11 | Number of times of restart after fault | P6.01 | Auto Restart after Fault | P06.04 | Auto Restart after Fault
358 | P07 Special | P07.12 | Speed tracking during start-up |  |  | P06.07 | Speed Search at Start
359 | P07 Special | P07.13 | dEb function selection |  |  | P06.61 | Decel Energy Backup (DEB) Decel Selection
360 | P07 Special | P07.15 | Dwell time at acceleration |  |  | P06.65 | Dwell Time at Accel
361 | P07 Special | P07.16 | Dwell frequency at acceleration |  |  | P06.66 | Dwell Frequency at Accel
362 | P07 Special | P07.17 | Dwell time at deceleration |  |  | P06.67 | Dwell Time at Decel
363 | P07 Special | P07.18 | Dwell frequency at deceleration |  |  | P06.68 | Dwell Frequency at Decel
364 | P07 Special | P07.19 | Fan cooling control |  |  | P06.31 | Cooling Fan Control
365 | P07 Special | P07.20 | Emergency stop (EF) & force to stop selection |  |  | P03.56 | Emergency Stop (EF) & Force Stop Selection
366 | P07 Special | P07.21 | Automatic energy- saving setting |  |  | P02.23 | Automatic Energy-Saving Operation
367 | P07 Special | P07.22 | Energy-saving gain |  |  | P02.24 | Power Saving Gain
368 | P07 Special | P07.23 | Automatic voltage regulation (AVR) function | P6.04 | Auto Voltage Regulation | P06.10 | Auto Voltage Regulation
369 | P07 Special | P07.24 | Torque command filter time (V/F and SVC control mode) |  |  | P02.03 | Torque Compensation Filter
370 | P07 Special | P07.25 | Slip compensation filter time (V/F,SVC control mode) |  |  | P02.25 | Slip Compensation Filter
371 | P07 Special | P07.26 | Torque compensation gain (V/F and SVC control mode) | P2.02 | Auto-torque Boost | P02.02 | Torque Compensation Gain
372 | P07 Special | P07.27 | Slip compensation gain (V/F and SVC control mode) | P2.01 | Slip Compensation | P02.01 | Slip Compensation Gain
373 | P07 Special | P07.29 | Slip deviation level |  |  | P02.26 | Slip Deviation Level
374 | P07 Special | P07.30 | Over-slip deviation detection time |  |  | P02.27 | Slip Deviation Detection time
375 | P07 Special | P07.31 | Over-slip deviation treatment |  |  | P02.28 | Slip Deviation Treatment
376 | P07 Special | P07.32 | Motor oscillation compensation factor |  |  | P02.29 | Hunting Gain
377 | P07 Special | P07.33 | Auto-restart interval of fault |  |  | P06.05 | Reset Time for Auto Restart after fault
378 | P07 Special | P07.38 | PMSVC voltage feed forward gain
379 | P07 Special | P07.46 | OOB sampling time
380 | P07 Special | P07.47 | Number of OOB sampling times
381 | P07 Special | P07.48 | OOB average sampling angle
382 | P07 Special | P07.62 | dEb gain (Kp)
383 | P07 Special | P07.71 | Torque compensation gain (motor 2)
384 | P07 Special | P07.72 | Slip compensation gain (motor 2)
385 | P07 Special | P07.73 | Torque compensation gain (motor 3)
386 | P07 Special | P07.74 | Slip compensation gain (motor 3)
387 | P07 Special | P07.75 | Torque compensation gain (motor 4)
388 | P07 Special | P07.76 | Slip compensation gain (motor 4)
389 | P08 Hi Func PID | P08.00 | Terminal selection of PID feedback | P7.00 | Input Terminal for PID Feedback | P07.00 | PID Action/Mode
390 | P08 Hi Func PID | P08.01 | Proportional gain (P) | P7.20 | Proportional Control | P07.13 | Proportional Gain
391 | P08 Hi Func PID | P08.02 | Integral time (I) | P7.21 | Integral Control | P07.14 | Integral Time
392 | P08 Hi Func PID | P08.03 | Differential time (D) | P7.22 | Derivative Control | P07.15 | Derivative Value
393 | P08 Hi Func PID | P08.04 | Upper limit of integral control | P7.23 | Upper Bound for Integral Control | P07.16 | Upper Limit for Integral Time
394 | P08 Hi Func PID | P08.05 | PID output command limit (positive limit) | P7.25 | PID Output Frequency Limit | P07.18 | PID Output Frequency Limit
395 | P08 Hi Func PID | P08.06 | PID feedback value by communication protocol |  |  | P07.19 | PID Feedback Value
396 | P08 Hi Func PID | P08.07 | PID delay time | P7.24 | Derivative Filter Time Constant | P07.17 | Derivative Filter Time Constant
397 | P08 Hi Func PID | P08.08 | Feedback signal detection time | P7.26 | Feedback Signal Detection Time | P07.20 | Feedback Signal Detection Time
398 | P08 Hi Func PID | P08.09 | Feedback signal fault treatment | P7.27 | PID Feedback Loss | P07.21 | PID Feedback Loss
399 | P08 Hi Func PID | P08.10 | Sleep frequency |  |  | P07.29 | Sleep Reference
400 | P08 Hi Func PID | P08.11 | Wake-up frequency |  |  | P07.30 | Wake-up Reference
401 | P08 Hi Func PID | P08.12 | Sleep time |  |  | P07.31 | Sleep Time
402 | P08 Hi Func PID | P08.13 | PID feedback signal error deviation level | P3.18 | PID Deviation Level | P03.36 | PID Deviation Level
403 | P08 Hi Func PID | P08.14 | PID feedback signal error deviation detection time | P3.19 | PID Deviation Time | P03.37 | PID Deviation Time
404 | P08 Hi Func PID | P08.15 | PID feedback signal filter time
405 | P08 Hi Func PID | P08.16 | PID compensation selection |  |  | P07.24 | PID Offset Selection
406 | P08 Hi Func PID | P08.17 | PID compensation |  |  | P07.04 | PID Offset Value
407 | P08 Hi Func PID | P08.18 | Sleep mode function setting |  |  | P07.27 | Source of Sleep
408 | P08 Hi Func PID | P08.19 | Wake-up integral limit |  |  | P07.28 | Integral Limit During Sleep
409 | P08 Hi Func PID | P08.20 | PID mode selection |  |  | P07.25 | PID Mode Selection
410 | P08 Hi Func PID | P08.21 | Enable PID to change the operation direction |  |  | P07.26 | PID Reverse Enable
411 | P08 Hi Func PID | P08.22 | Wake-up delay time |  |  | P07.32 | Wake-up Delay Time
412 | P08 Hi Func PID | P08.23 | PID control flag
413 | P08 Hi Func PID | P08.26 | PID output command limit (reverse limit)
414 | P08 Hi Func PID | P08.27 | Acceleration / deceleration time for PID command
415 | P08 Hi Func PID | P08.29 | Frequency base corresponding to 100.00% PID
416 | P08 Hi Func PID | P08.31 | Proportional gain 2
417 | P08 Hi Func PID | P08.32 | Integral time 2
418 | P08 Hi Func PID | P08.33 | Differential time 2
419 | P08 Hi Func PID | P08.65 | PID target value source | P7.02 | PID Setpoint Source | P07.02 | PID Setpoint Source Display (when PID enabled, this parameter data will be mapped from P4.00~P4.01 dependent upon whether in Remote=4.00 or Local=4.01)
420 | P08 Hi Func PID | P08.66 | PID target value setting
421 | P08 Hi Func PID | P08.67 | Master and auxiliary reverse running cutoff frequency
422 | P08 Hi Func PID | P08.68 | PID deviation limit
423 | P08 Hi Func PID | P08.69 | Integral separation level
424 | P08 Hi Func PID | P08.70 | Smart start-up level
425 | P08 Hi Func PID | P08.71 | Smart start-up frequency command
426 | P08 Hi Func PID | P08.72 | Smart start-up acceleration time
427 | P08 Hi Func PID | P08.75 | PID2 parameter switch condition
428 | P08 Hi Func PID | P08.76 | PID2 parameter switch deviation 1
429 | P08 Hi Func PID | P08.77 | PID2 parameter switch deviation 2
430 | P08 Hi Func PID | P08.78 | Allowed reverse running time after start-up
431 | P09 Communication | P09.00 | Communication address | P9.00 | Communication Address | P09.00 | VFD Comm Address
432 | P09 Communication | P09.01 | COM1 transmission speed | P9.01 | Transmission Speed | P09.01 | Modbus Baud Rate
433 | P09 Communication | P09.02 | COM1 transmission fault treatment | P9.03 | Transmission Fault Treatment | P09.03 | Modbus Fault Select
434 | P09 Communication | P09.03 | COM1 time-out detection | P9.04 P9.05 | Time Out Detection Time Out Duration | P09.04 P09.05 | Modbus Time Out Detection Modbus Time Out Duration
435 | P09 Communication | P09.04 | COM1 communication protocol | P9.02 | Communication Protocol | P09.02 | Modbus Protocol
436 | P09 Communication | P09.09 | Communication response delay time | P9.05* | Time Out Duration | P09.35 | Response Delay Time
437 | P09 Communication | P09.10 | Communication main frequency
438 | P09 Communication | P09.11 | Block transfer 1 | P9.11 | Block Transfer Parameter 1 | P09.09 | Block Transfer Data Location 1
439 | P09 Communication | P09.12 | Block transfer 2 | P9.12 | Block Transfer Parameter 2 | P09.10 | Block Transfer Data Location 2
440 | P09 Communication | P09.13 | Block transfer 3 | P9.13 | Block Transfer Parameter 3 | P09.11 | Block Transfer Data Location 3
441 | P09 Communication | P09.14 | Block transfer 4 | P9.14 | Block Transfer Parameter 4 | P09.12 | Block Transfer Data Location 4
442 | P09 Communication | P09.15 | Block transfer 5 | P9.15 | Block Transfer Parameter 5 | P09.13 | Block Transfer Data Location 5
443 | P09 Communication | P09.16 | Block transfer 6 | P9.16 | Block Transfer Parameter 6 | P09.14 | Block Transfer Data Location 6
444 | P09 Communication | P09.17 | Block transfer 7 | P9.17 | Block Transfer Parameter 7 | P09.15 | Block Transfer Data Location 7
445 | P09 Communication | P09.18 | Block transfer 8 | P9.18 | Block Transfer Parameter 8 | P09.16 | Block Transfer Data Location 8
446 | P09 Communication | P09.19 | Block transfer 9 | P9.19 | Block Transfer Parameter 9 | P09.17 | Block Transfer Data Location 9
447 | P09 Communication | P09.20 | Block transfer 10 | P9.20 | Block Transfer Parameter 10 | P09.18 | Block Transfer Data Location 10
448 | P09 Communication | P09.21 | Block transfer 11 | P9.21 | Block Transfer Parameter 11 | P09.19 | Block Transfer Data Location 11
449 | P09 Communication | P09.22 | Block transfer 12 | P9.22 | Block Transfer Parameter 12 | P09.20 | Block Transfer Data Location 12
450 | P09 Communication | P09.23 | Block transfer 13 | P9.23 | Block Transfer Parameter 13 | P09.21 | Block Transfer Data Location 13
451 | P09 Communication | P09.24 | Block transfer 14 | P9.24 | Block Transfer Parameter 14 | P09.22 | Block Transfer Data Location 14
452 | P09 Communication | P09.25 | Block transfer 15 | P9.25 | Block Transfer Parameter 15 | P09.23 | Block Transfer Data Location 15
453 | P09 Communication | P09.26 | Block transfer 16 |  |  | P09.24 | Block Transfer Data Location 16
454 | P09 Communication | P09.30 | Communication decoding method
455 | P09 Communication | P09.33 | PLC command force to 0 |  |  | P09.85 | PLC Frequency Command Force to 0
456 | P09 Communication | P09.35 | PLC address |  |  | P09.37 | PLC Address
457 | P09 Communication | P09.60 | Communication card identification |  |  | P09.44 | Comm Card Type
458 | P09 Communication | P09.61 | Firmware version of communication card |  |  | P09.45 | Comm Card Version
459 | P09 Communication | P09.62 | Product code |  |  | P09.46 | Comm Card Production Code
460 | P09 Communication | P09.63 | Error code |  |  | P09.47 | Comm Card Fault Code
461 | P09 Communication | P09.74 | Set Comm Master Protocol
462 | P09 Communication | P09.75 | Communication card IP configuration (Ethernet) |  |  | P09.48 | Comm Card IP Configuration
463 | P09 Communication | P09.76 | Communication card IP address 1 (Ethernet) |  |  | P09.49 | Comm Card IP Address Octet 1
464 | P09 Communication | P09.77 | Communication card IP address 2 (Ethernet) |  |  | P09.50 | Comm Card IP Address Octet 2
465 | P09 Communication | P09.78 | Communication card IP address 3 (Ethernet) |  |  | P09.51 | Comm Card IP Address Octet 3
466 | P09 Communication | P09.79 | Communication card IP address 4 (Ethernet) |  |  | P09.52 | Comm Card IP Address Octet 4
467 | P09 Communication | P09.80 | Communication card address mask 1 (Ethernet) |  |  | P09.53 | Comm Card Mask Octet 1
468 | P09 Communication | P09.81 | Communication card address mask 2 (Ethernet) |  |  | P09.54 | Comm Card Mask Octet 2
469 | P09 Communication | P09.82 | Communication card address mask 3 (Ethernet) |  |  | P09.55 | Comm Card Mask Octet 3
470 | P09 Communication | P09.83 | Communication card address mask 4 (Ethernet) |  |  | P09.56 | Comm Card Mask Octet 4
471 | P09 Communication | P09.84 | Communication card gateway address 1 (Ethernet) |  |  | P09.57 | Comm Card Gateway Octet 1
472 | P09 Communication | P09.85 | Communication card gateway address 2 (Ethernet) |  |  | P09.58 | Comm Card Gateway Octet 2
473 | P09 Communication | P09.86 | Communication card gateway address 3 (Ethernet) |  |  | P09.59 | Comm Card Gateway Octet 3
474 | P09 Communication | P09.87 | Communication card gateway address 4 (Ethernet) |  |  | P09.60 | Comm Card Gateway Octet 4
475 | P09 Communication | P09.88 | Communication card password (low word) (Ethernet)
476 | P09 Communication | P09.89 | Communication card password (high word) (Ethernet)
477 | P09 Communication | P09.90 | Reset communication card (Ethernet) |  |  | P09.63 | Comm Card Factory Reset
478 | P09 Communication | P09.91 | Additional settings for the communication card (Ethernet)
479 | P09 Communication | P09.92 | Communication card status (Ethernet)
480 | P09 Communication | P09.93 | ENETIP Comm Card Fault Select |  |  | P09.93 | Ethernet Comm Card Fault Select
481 | P09 Communication | P09.94 | ENETIP Comm Card Time Out Detection |  |  | P09.94 | Ethernet Comm Card Time Out Detection
482 | P09 Communication | P09.95 | ENETIP Comm Card Time Out Duration |  |  | P09.95 | Ethernet Comm Card Time Out Duration
483 | P10 Spd Fdbk Control | P10.00 | Encoder type selection
484 | P10 Spd Fdbk Control | P10.01 | Encoder pulses per revolution
485 | P10 Spd Fdbk Control | P10.02 | Encoder input type setting
486 | P10 Spd Fdbk Control | P10.04 | Electrical gear at load side A1
487 | P10 Spd Fdbk Control | P10.05 | Electrical gear at motor side B1
488 | P10 Spd Fdbk Control | P10.06 | Electrical gear at load side A2
489 | P10 Spd Fdbk Control | P10.07 | Electrical gear at motor side B2
490 | P10 Spd Fdbk Control | P10.10 | Encoder stall level
491 | P10 Spd Fdbk Control | P10.11 | Detection time of encoder stall
492 | P10 Spd Fdbk Control | P10.12 | Encoder stall action
493 | P10 Spd Fdbk Control | P10.13 | Encoder slip range
494 | P10 Spd Fdbk Control | P10.14 | Detection time of encoder slip
495 | P10 Spd Fdbk Control | P10.15 | Encoder stall and slip error action
496 | P10 Spd Fdbk Control | P10.16 | Pulse input type setting
497 | P10 Spd Fdbk Control | P10.17 | Electrical gear A
498 | P10 Spd Fdbk Control | P10.18 | Electrical gear B
499 | P10 Spd Fdbk Control | P10.21 | PG2 (DI7) pulse input speed command low pass filter time
500 | P10 Spd Fdbk Control | P10.24 | FOC & TQC function control
501 | P10 Spd Fdbk Control | P10.25 | FOC bandwidth for speed observer
502 | P10 Spd Fdbk Control | P10.26 | FOC minimum stator frequency
503 | P10 Spd Fdbk Control | P10.27 | FOC low pass filter time constant
504 | P10 Spd Fdbk Control | P10.28 | FOC gain for excitation current rise time
505 | P10 Spd Fdbk Control | P10.29 | Upper limit of frequency deviation
506 | P10 Spd Fdbk Control | P10.31 | I/F mode, current command
507 | P10 Spd Fdbk Control | P10.32 | PM sensorless speed estimator bandwidth
508 | P10 Spd Fdbk Control | P10.34 | PM sensorless speed estimator low-pass filter gain
509 | P10 Spd Fdbk Control | P10.35 | Active Magnetic Regulator (AMR) (Kp) gain
510 | P10 Spd Fdbk Control | P10.36 | Active Magnetic Regulator (AMR) (Ki) gain
511 | P10 Spd Fdbk Control | P10.39 | Frequency point to switch from I/F mode to PM sensorless mode
512 | P10 Spd Fdbk Control | P10.42 | Initial angle detection pulse value
513 | P10 Spd Fdbk Control | P10.49 | Zero voltage time during start-up
514 | P10 Spd Fdbk Control | P10.51 | Injection frequency
515 | P10 Spd Fdbk Control | P10.52 | Injection magnitude
516 | P10 Spd Fdbk Control | P10.53 | Angle detection method
517 | P11 Advanced | P11.00 | System control
518 | P11 Advanced | P11.01 | Per-unit of system inertia
519 | P11 Advanced | P11.02 | ASR1/ASR2 switch frequency
520 | P11 Advanced | P11.03 | ASR1 low-speed bandwidth
521 | P11 Advanced | P11.04 | ASR2 high-speed bandwidth
522 | P11 Advanced | P11.05 | Zero-speed bandwidth
523 | P11 Advanced | P11.06 | ASR1 (Kp) gain
524 | P11 Advanced | P11.07 | ASR1 (Ki) integral time
525 | P11 Advanced | P11.08 | ASR2 (Kp) gain
526 | P11 Advanced | P11.09 | ASR2 (Ki) integral time
527 | P11 Advanced | P11.10 | ASR Kp gain of zero speed
528 | P11 Advanced | P11.11 | ASR (Ki) integral time of zero speed
529 | P11 Advanced | P11.12 | Gain for ASR speed feed forward
530 | P11 Advanced | P11.13 | PDFF gain value
531 | P11 Advanced | P11.14 | ASR output low pass filter time
532 | P11 Advanced | P11.15 | Notch filter depth
533 | P11 Advanced | P11.16 | Notch filter frequency
534 | P11 Advanced | P11.17 | Forward motor torque limit
535 | P11 Advanced | P11.18 | Forward regenerative torque limit
536 | P11 Advanced | P11.19 | Reverse motor torque limit
537 | P11 Advanced | P11.20 | Reverse regenerative torque limit
538 | P11 Advanced | P11.21 | Flux weakening curve for motor 1 gain value
539 | P11 Advanced | P11.22 | Flux weakening curve for motor 2 gain value
540 | P11 Advanced | P11.23 | Flux weakening area speed response
541 | P11 Advanced | P11.27 | Maximum torque command
542 | P11 Advanced | P11.28 | Torque offset source
543 | P11 Advanced | P11.29 | Torque offset setting
544 | P11 Advanced | P11.30 | High torque offset
545 | P11 Advanced | P11.31 | Middle torque offset
546 | P11 Advanced | P11.32 | Low torque offset
547 | P11 Advanced | P11.33 | Torque command source
548 | P11 Advanced | P11.34 | Torque command
549 | P11 Advanced | P11.35 | Torque command filter time
550 | P11 Advanced | P11.36 | Speed limit selection
551 | P11 Advanced | P11.37 | Forward speed limit (Torque mode)
552 | P11 Advanced | P11.38 | Reverse speed limit (Torque mode)
553 | P11 Advanced | P11.41 | PWM mode selection
554 | P11 Advanced | P11.42 | System control flag
555 | P13 Macro/User | P13.00 | Industry-specific parameter application | P2.00 | Volts/Hertz Settings | P02.00 | Volts/Hertz Settings
556 | P13 Macro/User | P13.01 | User-defined parameter
557 | P13 Macro/User | P13.02 | User-defined parameter
558 | P13 Macro/User | P13.03 | User-defined parameter
559 | P13 Macro/User | P13.04 | User-defined parameter
560 | P13 Macro/User | P13.05 | User-defined parameter
561 | P13 Macro/User | P13.06 | User-defined parameter
562 | P13 Macro/User | P13.07 | User-defined parameter
563 | P13 Macro/User | P13.08 | User-defined parameter
564 | P13 Macro/User | P13.09 | User-defined parameter
565 | P13 Macro/User | P13.10 | User-defined parameter
566 | P13 Macro/User | P13.11 | User-defined parameter
567 | P13 Macro/User | P13.12 | User-defined parameter
568 | P13 Macro/User | P13.13 | User-defined parameter
569 | P13 Macro/User | P13.14 | User-defined parameter
570 | P13 Macro/User | P13.15 | User-defined parameter
571 | P13 Macro/User | P13.16 | User-defined parameter
572 | P13 Macro/User | P13.17 | User-defined parameter
573 | P13 Macro/User | P13.18 | User-defined parameter
574 | P13 Macro/User | P13.19 | User-defined parameter
575 | P13 Macro/User | P13.20 | User-defined parameter
576 | P13 Macro/User | P13.21 | User-defined parameter
577 | P13 Macro/User | P13.22 | User-defined parameter
578 | P13 Macro/User | P13.23 | User-defined parameter
579 | P13 Macro/User | P13.24 | User-defined parameter
580 | P13 Macro/User | P13.25 | User-defined parameter
581 | P13 Macro/User | P13.26 | User-defined parameter
582 | P13 Macro/User | P13.27 | User-defined parameter
583 | P13 Macro/User | P13.28 | User-defined parameter
584 | P13 Macro/User | P13.29 | User-defined parameter
585 | P13 Macro/User | P13.30 | User-defined parameter
586 | P13 Macro/User | P13.31 | User-defined parameter
587 | P13 Macro/User | P13.32 | User-defined parameter
588 | P13 Macro/User | P13.33 | User-defined parameter
589 | P13 Macro/User | P13.34 | User-defined parameter
590 | P13 Macro/User | P13.35 | User-defined parameter
591 | P13 Macro/User | P13.36 | User-defined parameter
592 | P13 Macro/User | P13.37 | User-defined parameter
593 | P13 Macro/User | P13.38 | User-defined parameter
594 | P13 Macro/User | P13.39 | User-defined parameter
595 | P13 Macro/User | P13.40 | User-defined parameter
596 | P13 Macro/User | P13.41 | User-defined parameter
597 | P13 Macro/User | P13.42 | User-defined parameter
598 | P13 Macro/User | P13.43 | User-defined parameter
599 | P13 Macro/User | P13.44 | User-defined parameter
600 | P13 Macro/User | P13.45 | User-defined parameter
601 | P13 Macro/User | P13.46 | User-defined parameter
602 | P13 Macro/User | P13.47 | User-defined parameter
603 | P13 Macro/User | P13.48 | User-defined parameter
604 | P13 Macro/User | P13.49 | User-defined parameter
605 | P13 Macro/User | P13.50 | User-defined parameter
606 | P14 Protection(2) | P14.50 | Output frequency at malfunction 2
607 | P14 Protection(2) | P14.51 | DC bus voltage at malfunction 2
608 | P14 Protection(2) | P14.52 | Output current at malfunction 2
609 | P14 Protection(2) | P14.53 | IGBT temperature at malfunction 2
610 | P14 Protection(2) | P14.54 | Output frequency at malfunction 3
611 | P14 Protection(2) | P14.55 | DC bus voltage at malfunction 3
612 | P14 Protection(2) | P14.56 | Output current at malfunction 3
613 | P14 Protection(2) | P14.57 | IGBT temperature at malfunction 3
614 | P14 Protection(2) | P14.58 | Output frequency at malfunction 4
615 | P14 Protection(2) | P14.59 | DC bus voltage at malfunction 4
616 | P14 Protection(2) | P14.60 | Output current at malfunction 4
617 | P14 Protection(2) | P14.61 | IGBT temperature at malfunction 4
618 | P14 Protection(2) | P14.62 | Output frequency at malfunction 5
619 | P14 Protection(2) | P14.63 | DC bus voltage at malfunction 5
620 | P14 Protection(2) | P14.64 | Output current at malfunction 5
621 | P14 Protection(2) | P14.65 | IGBT temperature at malfunction 5
622 | P14 Protection(2) | P14.66 | Output frequency at malfunction 6
623 | P14 Protection(2) | P14.67 | DC bus voltage at malfunction 6
624 | P14 Protection(2) | P14.68 | Output current at malfunction 6
625 | P14 Protection(2) | P14.69 | IGBT temperature at malfunction 6
626 | P14 Protection(2) | P14.70 | Fault record 7
627 | P14 Protection(2) | P14.71 | Fault record 8
628 | P14 Protection(2) | P14.72 | Fault record 9
629 | P14 Protection(2) | P14.73 | Fault record 10
630 | P14 Protection(2) | P14.74 | Over-torque detection selection (motor 3)
631 | P14 Protection(2) | P14.75 | Over-torque detection level (motor 3)
632 | P14 Protection(2) | P14.76 | Over-torque detection time (motor 3)
633 | P14 Protection(2) | P14.77 | Over-torque detection selection (motor 4)
634 | P14 Protection(2) | P14.78 | Over-torque detection level (motor 4)
635 | P14 Protection(2) | P14.79 | Over-torque detection time (motor 4)
636 | P14 Protection(2) | P14.80 | Electronic thermal relay selection 3 (motor 3)
637 | P14 Protection(2) | P14.81 | Electronic thermal relay action time 3 (motor 3)
638 | P14 Protection(2) | P14.82 | Electronic thermal relay selection 4 (motor 4)
639 | P14 Protection(2) | P14.83 | Electronic thermal relay action time 4 (motor 4)
640 |  | xN/A |  | P1.09 | Decel 2 to Decel 1 frequency transition
641 |  | xN/A |  | P1.17 | Skip Frequency Band
642 |  | xN/A |  |  |  | P03.10 | Multi-Function Input (DI8)
643 |  | xN/A |  |  |  | P03.11 | Multi-Function Input (option card DI10 or PLC X12)
644 |  | xN/A |  |  |  | P03.12 | Multi-Function Input (option card DI11 or PLC X13)
645 |  | xN/A |  |  |  | P03.13 | Multi-Function Input (option card DI12 or PLC X14)
646 |  | xN/A |  |  |  | P03.14 | Multi-Function Input (option card DI13 or PLC X15)
647 |  | xN/A |  |  |  | P03.15 | Multi-Function Input (option card DI14 or PLC X16)
648 |  | xN/A |  |  |  | P03.16 | Multi-Function Input (option card DI15 or PLC X17)
649 |  | xN/A |  |  |  | P03.18 | Multi-Function Output Terminal 2 (Relay 2 or PLC Y1)
650 |  | xN/A |  |  |  | P03.21 | Multi-Function Output Terminal 5 (option card DO10 or RO10, or PLC Y5)
651 |  | xN/A |  |  |  | P03.22 | Multi-Function Output Terminal 6 (option card DO11 or RO11, or PLC Y6)
652 |  | xN/A |  |  |  | P03.23 | Multi-Function Output Terminal 7 (option card RO12 or PLC Y7)
653 |  | xN/A |  |  |  | P03.24 | Multi-Function Output Terminal 8 (option card RO13 or PLC Y10)
654 |  | xN/A |  |  |  | P03.25 | Multi-Function Output Terminal 9 (option card RO14 or PLC Y11)
655 |  | xN/A |  |  |  | P03.26 | Multi-Function Output Terminal 10 (option card RO15 or PLC Y12)
656 |  | xN/A |  |  |  | P03.27 | Multi-Function Virtual Output 11 (DO16, PLC Y13)
657 |  | xN/A |  |  |  | P03.28 | Multi-Function Virtual Output 12 (DO17, PLC Y14)
658 |  | xN/A |  |  |  | P03.29 | Multi-Function Virtual Output 13 (DO18, PLC Y15)
659 |  | xN/A |  |  |  | P03.30 | Multi-Function Virtual Output 14 (DO19, PLC Y16)
660 |  | xN/A |  |  |  | P03.31 | Multi-Function Virtual Output 15 (DO20, PLC Y17)
661 |  | xN/A |  | P3.17 | Desired Current | P03.52 | Desired Current
662 |  | xN/A |  |  |  | P03.54 | reserved
663 |  | xN/A |  |  |  | P03.55 | reserved
664 |  | xN/A |  |  |  | P03.57 | AUTO to HAND Switching Behavior
675 |  | xN/A |  |  |  | P04.04 | Analog Input 3 (AI3) Function
676 |  | xN/A |  |  |  | P04.07 | Trim Reference Frequency
677 |  | xN/A |  |  |  | P04.08 | Trim Selection
678 |  | xN/A |  |  |  | P04.14 | reserved
679 |  | xN/A |  |  |  | P04.19 | AI3 Input Bias (Offset)
680 |  | xN/A |  |  |  | P04.20 | AI3 Input Bias (Offset) Polarity
681 |  | xN/A |  |  |  | P04.21 | +AI3 Input Gain
682 |  | xN/A |  |  |  | P04.22 | -AI3 Input Gain
683 |  | xN/A |  |  |  | P04.23 | AI3 Filter
684 |  | xN/A |  |  |  | P04.37 | AI3 Low Voltage Unipolar
685 |  | xN/A |  |  |  | P04.38 | AI3 Low Hz Percent Unipolar
686 |  | xN/A |  |  |  | P04.39 | AI3 Mid Voltage Unipolar
687 |  | xN/A |  |  |  | P04.40 | AI3 Mid Hz Percent Unipolar
688 |  | xN/A |  |  |  | P04.41 | AI3 High Voltage Unipolar
689 |  | xN/A |  |  |  | P04.42 | AI3 High Hz Percent Unipolar
690 |  | xN/A |  |  |  | P04.49 | reserved
691 |  | xN/A |  |  |  | P04.54 | Analog Output 2 (AO2)
692 |  | xN/A |  |  |  | P04.55 | AO2 Gain
693 |  | xN/A |  |  |  | P04.56 | AO2 Negative Value Handle
694 |  | xN/A |  |  |  | P04.57 | AO2 0~20mA/4~20mA Selection
695 |  | xN/A |  |  |  | P04.58 | reserved
696 |  | xN/A |  |  |  | P04.59 | AO2 Offset (Bias)
697 |  | xN/A |  |  |  | P04.61 | AO2 Output Constant Level
698 |  | xN/A |  |  |  | P04.63 | Loss of AI1 Signal (4~20mA)
699 |  | xN/A |  |  |  | P06.32 | PWM Fan Speed
700 |  | xN/A |  |  |  | P06.57 | Fire Mode Enable Bypass
701 |  | xN/A |  |  |  | P06.58 | Fire Mode Bypass Delay Time
702 |  | xN/A |  |  |  | P06.59 | Fire Mode Auto Restart Counter
703 |  | xN/A |  |  |  | P06.60 | Fire Mode Auto Restart Counter Reset Time
704 |  | xN/A |  |  |  | P06.62 | DEB Offset Level
705 |  | xN/A |  |  |  | P06.63 | DEB Disable Voltage Level
706 |  | xN/A |  |  |  | P06.64 | DEB Delay Time
707 |  | xN/A |  |  |  | P07.01 | reserved
708 |  | xN/A |  |  |  | P07.03 | PID Feedback Gain
709 |  | xN/A |  | P7.10 | Keypad PID Setpoint | P07.05 | Keypad PID Setpoint
710 |  | xN/A | Use PLC function with inputs | P7.11 | PID Multi-setpoint 1 | P07.06 | PID Multi-Setpoint 1
711 |  | xN/A | Use PLC function with inputs | P7.12 | PID Multi-setpoint 2 | P07.07 | PID Multi-Setpoint 2
712 |  | xN/A | Use PLC function with inputs | P7.13 | PID Multi-setpoint 3 | P07.08 | PID Multi-Setpoint 3
713 |  | xN/A | Use PLC function with inputs | P7.14 | PID Multi-setpoint 4 | P07.09 | PID Multi-Setpoint 4
714 |  | xN/A | Use PLC function with inputs | P7.15 | PID Multi-setpoint 5 | P07.10 | PID Multi-Setpoint 5
715 |  | xN/A | Use PLC function with inputs | P7.16 | PID Multi-setpoint 6 | P07.11 | PID Multi-Setpoint 6
716 |  | xN/A | Use PLC function with inputs | P7.17 | PID Multi-setpoint 7 | P07.12 | PID Multi-Setpoint 7
717 |  | xN/A |  |  |  | P07.22 | PID Feedback Loss Speed Level Default
718 |  | xN/A |  |  |  | P07.23 | reserved
719 |  | xN/A |  |  |  | P08.08 | Power On Counter
720 |  | xN/A |  |  |  | P08.09 | Power On Day
721 |  | xN/A |  |  |  | P08.10 | Power On Minute
722 |  | xN/A |  |  |  | P08.13 | Keypad Communication Fault Treatment
723 |  | xN/A |  |  |  | P08.14 | Keypad Time Out
724 |  | xN/A |  |  |  | P08.15 | reserved
725 |  | xN/A |  |  |  | P08.16 | reserved
726 |  | xN/A |  |  |  | P08.17 | reserved
727 |  | xN/A |  |  |  | P08.18 | reserved
728 |  | xN/A |  |  |  | P08.19 | reserved
729 |  | xN/A |  |  |  | P09.06 | Parameter Copy
730 |  | xN/A |  |  |  | P09.25 | reserved
731 |  | xN/A | Use 2000, 2001, 2002 words | P9.26 | Serial Comm Speed Reference | P09.26 | RS485 Speed Reference
732 |  | xN/A | Use 2000, 2001, 2002 words | P9.27 | Serial Comm RUN Command | P09.27 | RS485 RUN Command
733 |  | xN/A | Use 2000, 2001, 2002 words | P9.28 | Serial Comm Direction Command | P09.28 | RS485 Direction Command
734 |  | xN/A | Use 2000, 2001, 2002 words | P9.29 | Serial Comm External Fault | P09.29 | RS485 External Fault
735 |  | xN/A | Use 2000, 2001, 2002 words | P9.30 | Serial Comm Fault Reset | P09.30 | RS485 Fault Reset
736 |  | xN/A | Use 2000, 2001, 2002 words | P9.31 | Serial Comm JOG Command | P09.31 | RS485 JOG Command
737 |  | xN/A |  |  |  | P09.32 | reserved
738 |  | xN/A |  |  |  | P09.36 | reserved
739 |  | xN/A |  |  |  | P09.38 | Firmware Date Code
740 |  | xN/A |  |  |  | P09.40 | reserved
741 |  | xN/A | TBD | P9.41 | GS Series Number | P09.41 | GS Series Number
742 |  | xN/A |  |  |  | P09.43 | Ignore Comm Card Warning
743 |  | xN/A |  |  |  | P09.61 | reserved
744 |  | xN/A |  |  |  | P09.62 | reserved
745 |  | xN/A |  |  |  | P09.64 | Comm Card External Set
746 |  | xN/A |  |  |  | P09.65 | reserved
747 |  | xN/A |  |  |  | P09.66 | reserved
748 |  | xN/A |  |  |  | P09.67 | reserved
749 |  | xN/A |  |  |  | P09.68 | reserved
750 |  | xN/A |  |  |  | P09.69 | Block Transfer Address Pointer 1
751 |  | xN/A |  |  |  | P09.70 | Block Transfer Address Pointer 2
752 |  | xN/A |  |  |  | P09.71 | Block Transfer Address Pointer 3
753 |  | xN/A |  |  |  | P09.72 | Block Transfer Address Pointer 4
754 |  | xN/A |  |  |  | P09.73 | Block Transfer Address Pointer 5
755 |  | xN/A |  |  |  | P09.74 | Block Transfer Address Pointer 6
756 |  | xN/A |  |  |  | P09.75 | Block Transfer Address Pointer 7
757 |  | xN/A |  |  |  | P09.76 | Block Transfer Address Pointer 8
758 |  | xN/A |  |  |  | P09.77 | Block Transfer Address Pointer 9
759 |  | xN/A |  |  |  | P09.78 | Block Transfer Address Pointer 10
760 |  | xN/A |  |  |  | P09.79 | Block Transfer Address Pointer 11
761 |  | xN/A |  |  |  | P09.80 | Block Transfer Address Pointer 12
762 |  | xN/A |  |  |  | P09.81 | Block Transfer Address Pointer 13
763 |  | xN/A |  |  |  | P09.82 | Block Transfer Address Pointer 14
764 |  | xN/A |  |  |  | P09.83 | Block Transfer Address Pointer 15
765 |  | xN/A |  |  |  | P09.84 | Block Transfer Address Pointer 16
766 |  | xN/A |  |  |  | P09.86 | COMM1 Protocol (via RS-485)
767 |  | xN/A |  |  |  | P09.87 | BACnet Address
768 |  | xN/A |  |  |  | P09.88 | BACnet Baud Rate
769 |  | xN/A |  |  |  | P09.89 | BACnet Device Instance Low Word
770 |  | xN/A |  |  |  | P09.90 | BACnet Device Instance High Byte
771 |  | xN/A |  |  |  | P09.91 | BACnet Max Polling Address
772 |  | xN/A |  |  |  | P09.92 | BACnet Password
773 |  | xN/A |  |  |  | P09.96 | reserved
774 |  | xN/A |  |  |  | P09.97 | reserved
775 |  | xN/A |  |  |  | P09.98 | reserved
776 |  | xN/A |  |  |  | P09.99 | reserved
777 |  | xN/A |  |  |  | P10.00 | Circulative Control
778 |  | xN/A |  |  |  | P10.01 | Number of Connected Motors
779 |  | xN/A |  |  |  | P10.02 | Desired Run Time of Each Motor in Minutes
780 |  | xN/A |  |  |  | P10.03 | Motor Switch Delay Time During Increasing Demand
781 |  | xN/A |  |  |  | P10.04 | Motor Switch Delay Time During Decreasing Demand
782 |  | xN/A |  |  |  | P10.05 | Aux Motor Switch Delay Time During Fix Amount Circulation in Seconds
783 |  | xN/A |  |  |  | P10.06 | Aux Motor Switch Frequency During Fix Amount Circulation in Hz
784 |  | xN/A |  |  |  | P10.07 | Circulative Control Malfunction Action
785 |  | xN/A |  |  |  | P10.08 | AUX Motor Stop Frequency
786 |  | xN/A |  |  |  | P11.24 | HeatSink Temperature at Fault
787

## CrossRef_GS4 full
DURAPULSE GS4 PARAMETER SUMMARY | [7 empty] | DURAPULSE GS20 & GS20X PARAMETER SUMMARY | [7 empty] | SEE DISCLAIMER
GS4 Seq | Parameter Group | Parameter No. | Parameter Description | Range | Range (cont) | R/W | Default | GS20Seq | Parameter Group | Parameter No. | Parameter Description | Range | Range (con't) | R/W | Default
1 | P00 Motor | P0.00 | Motor 1 Maximum Output Voltage | 230V: 0.0~255.0V 460V: 0.0~510.0V |  | R/W | GS4-2xxx: 230.0 GS4-4xxx: 460.0 | 36 | P01 Basic | P01.02 | Motor 1, Rated Voltage (Nameplate) | 120V / 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V 575V models: 0.0-637.0 V |  | R/W | 220.0 440.0 575.0
2 | P00 Motor | P0.01 | Motor 1 Rated Current | 10~120% drive rated Amps |  | R/W | 90% rated I of GS4 | 225 | P05 Motor | P05.01 | Induction Motor 1, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
3 | P00 Motor | P0.02 | Motor 1 Base Frequency | 0.00~600.00 Hz |  | R/W | 60 | 35 | P01 Basic | P01.01 | Motor 1 Fbase | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
4 | P00 Motor | P0.03 | Motor 1 Rated RPM | 0 to (120 x P0.02/P0.09)-1 |  | ♦R/W | 1710 (60Hz 4-pole) 1410 (50Hz 4-pole) | 227 | P05 Motor | P05.03 | Induction Motor 1, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
5 | P00 Motor | P0.04 | Drive Maximum Output Frequency | 0~600.00 Hz |  | R/W | 50.00/60.00 | 34 | P01 Basic | P01.00 | Maximum operation frequency | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
6 | P00 Motor | P0.05 | Motor Auto Tune | 0: Disable 1: Measure motor in dynamic status (motor spinning) 2: Measure motor in static status (motor not spinning) |  | R/W | 0 | 224 | P05 Motor | P05.00 | Motor parameter auto-tuning | 0: No function 1: Dynamic test for induction motor (IM) 2: Static test for induction motor (IM) 5: Rolling auto-tuning for PM (IPM / SPM) 6: Simple rolling auto-tuning for induction motor (IM) 12: FOC sensorless inertia estimation 13: High frequency stall test for PM |  | R/W | 0
7 | P00 Motor | P0.06 | Motor 1 Resistance | 0~65.5350 |  | R/W | 0 | 230 | P05 Motor | P05.06 | Induction Motor 1, Stator resistance (Rs) | 0.000-65.535 0 |  | R/W | Model dependent
8 | P00 Motor | P0.07 | Motor 1 No-Load Current | 0~100% motor rated Amps |  | R/W | 40% of Motor1 Rated I | 229 | P05 Motor | P05.05 | Induction Motor 1, No-load amps | 0.00-P05.01 default |  | R/W | Model dependent
9 | P00 Motor | P0.08 | Motor 1 Rated Horsepower (HP) | 0.00~655.35hp |  | ♦R/W | Rated hp of GS4 | 226 | P05 Motor | P05.02 | Induction Motor 1, Rated power (kW) | 0.00-655.35 kW |  | ♦R/W | Model dependent
10 | P00 Motor | P0.09 | Motor 1 Number of Poles | 2 to (120 x P0.02/P0.03) |  | R/W | 4 | 228 | P05 Motor | P05.04 | Induction Motor 1, Number of poles | 2-20 |  | R/W | 4
11 | P00 Motor | P0.10 | Motor 1 or 2 Selection | 1: Motor 1 2: Motor 2 |  | R/W | 1 | 243 | P05 Motor | P05.22 | Multi-motor (induction) selection | 1: Motor 1 2: Motor 2 3: Motor 3 (VF or SVC control mode only) 4: Motor 4 (VF or SVC control mode only) |  | R/W | 1
12 | P00 Motor | P0.11 | Motor 2 Maximum Output Voltage | 230V: 0.0~255.0V 460V: 0.0~510.0V |  | R/W | GS4-2xxx: 230.00 GS4-4xxx: 460.00 | 70 | P01 Basic | P01.36 | Motor 2, Output voltage (Base voltage / Motor's rated voltage) | 120V / 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V 575V models: 0.0-637.0 V |  | R/W | 220.0 440.0 575.0
13 | P00 Motor | P0.12 | Motor 2 Rated Current | 10~120% drive rated Amps |  | R/W | 90% rated I of GS4 | 234 | P05 Motor | P05.13 | Induction Motor 2, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
14 | P00 Motor | P0.13 | Motor 2 Base Frequency | 0.00~600.00 Hz |  | R/W | 60 | 69 | P01 Basic | P01.35 | Motor 2, Output frequency (Base frequency / Motor's rated frequency) | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
15 | P00 Motor | P0.14 | Motor 2 Rated RPM | 0 to [(120 x P0.13/P0.18)-1] rpm |  | ♦R/W | 1710 (60Hz 4-pole) 1410 (50Hz 4-pole) | 236 | P05 Motor | P05.15 | Induction Motor 2, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
16 | P00 Motor | P0.15 | Motor 2 Resistance | 0~65.5350 |  | R/W | 0 | 239 | P05 Motor | P05.18 | Induction Motor 2, Stator resistance (Rs) | 0.000-65.535 0 |  | R/W | Model dependent
17 | P00 Motor | P0.16 | Motor 2 No-Load Current | 0~100% motor rated Amps |  | R/W | 40% of Motor2 Rated I | 238 | P05 Motor | P05.17 | Induction Motor 2, No- load amps | 0.00-P05.13 default |  | R/W | Model dependent
18 | P00 Motor | P0.17 | Motor 2 Rated Horsepower (HP) | 0.00~655.35 hp |  | ♦R/W | Rated hp of GS4 | 235 | P05 Motor | P05.14 | Induction Motor 2, Rated power (kW) | 0.00-655.35 kW |  | ♦R/W | Model dependent
19 | P00 Motor | P0.18 | Motor 2 Number of Poles | 2 to (120 x P0.13/P0.14) |  | R/W | 4 | 237 | P05 Motor | P05.16 | Induction Motor 2, Number of poles | 2-20 |  | R/W | 4
20 | P01 Ramps | P01.00 | Stop Method | 0: Ramp to stop 1: Coast to stop |  | ♦R/W | 0 | 18 | P00 Drive | P00.22 | Stop method | 0: Ramp to stop 1: Coast to stop |  | ♦R/W | 0
21 | P01 Ramps | P01.01 | Acceleration Time 1 | P1.15=0: 0.00~600.00 sec P1.15=1: 0.0~6000.0 sec |  | ♦R/W | 10 | 46 | P01 Basic | P01.12 | Acceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
22 | P01 Ramps | P01.02 | Deceleration Time 1 |  |  | ♦R/W | 10 | 47 | P01 Basic | P01.13 | Deceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
23 | P01 Ramps | P01.03 | Acceleration Time 2 |  |  | ♦R/W | 10 | 48 | P01 Basic | P01.14 | Acceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
24 | P01 Ramps | P01.04 | Deceleration Time 2 |  |  | ♦R/W | 10 | 49 | P01 Basic | P01.15 | Deceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
25 | P01 Ramps | P01.05 | Acceleration Time 3 |  |  | ♦R/W | 10 | 50 | P01 Basic | P01.16 | Acceleration time 3 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
26 | P01 Ramps | P01.06 | Deceleration Time 3 |  |  | ♦R/W | 10 | 51 | P01 Basic | P01.17 | Deceleration time 3 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
27 | P01 Ramps | P01.07 | Acceleration Time 4 |  |  | ♦R/W | 10 | 52 | P01 Basic | P01.18 | Acceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
28 | P01 Ramps | P01.08 | Deceleration Time 4 |  |  | ♦R/W | 10 | 53 | P01 Basic | P01.19 | Deceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
29 | P01 Ramps | P01.09 | S-curve Accel Time 1 | P1.15=0: 0.00~25.00 sec P1.15=1: 0.0~250.0 sec |  | ♦R/W | 0.2 | 58 | P01 Basic | P01.24 | S-curve for acceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
30 | P01 Ramps | P01.10 | S-curve Decel Time 1 |  |  | ♦R/W | 0.2 | 60 | P01 Basic | P01.26 | S-curve for deceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
31 | P01 Ramps | P01.11 | S-curve Accel Time 2 |  |  | ♦R/W | 0.2 | 59 | P01 Basic | P01.25 | S-curve for acceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
32 | P01 Ramps | P01.12 | S-curve Decel Time 2 |  |  | ♦R/W | 0.2 | 61 | P01 Basic | P01.27 | S-curve for deceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
33 | P01 Ramps | P01.13 | Jog Acceleration Time | P1.15=0: 0.00~600.00 sec P1.15=1: 0.0~6000.0 sec |  | ♦R/W | 10 | 54 | P01 Basic | P01.20 | JOG acceleration time | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
34 | P01 Ramps | P01.14 | Jog Deceleration Time |  |  | ♦R/W | 10 | 55 | P01 Basic | P01.21 | JOG deceleration time | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
35 | P01 Ramps | P01.15 | Time Unit for Accel/Decel & S-curve | 0: unit 0.01sec 1: unit 0.1sec |  | R/W | 1 | 79 | P01 Basic | P01.45 | Time unit for acceleration / deceleration and S-curve | 0: Unit 0.01 sec. 1: Unit 0.1 sec. |  | R/W | 0
36 | P01 Ramps | P01.16 | Accel/Decel Transition Method | 0: rmp2 from terminal 1: transition frequencies P1.17 & P1.18 |  | ♦R/W | 0 | 57 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | 0.00-599.00 Hz |  | ♦R/W | 0
37 | P01 Ramps | P01.17 | Accel Transition Frequency 1-2 | 0.00~600.00 Hz |  | ♦R/W | 0 | 57 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | 0.00-599.00 Hz |  | ♦R/W | 0
38 | P01 Ramps | P01.18 | Decel Transition Frequency 1-2 |  |  | ♦R/W | 0 | 57 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | 0.00-599.00 Hz |  | ♦R/W | 0
39 | P01 Ramps | P01.19 | Skip Frequency 1 Upper Limit | 0.00~600.00 Hz |  | R/W | 0 | 62 | P01 Basic | P01.28 | Skip frequency 1 (upper limit) | 0.00-599.00 Hz |  | R/W | 0
40 | P01 Ramps | P01.20 | Skip Frequency 1 Lower Limit |  |  | R/W | 0 | 63 | P01 Basic | P01.29 | Skip frequency 1 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
41 | P01 Ramps | P01.21 | Skip Frequency 2 Upper Limit |  |  | R/W | 0 | 64 | P01 Basic | P01.30 | Skip frequency 2 (upper limit) | 0.00-599.00 Hz |  | R/W | 0
42 | P01 Ramps | P01.22 | Skip Frequency 2 Lower Limit |  |  | R/W | 0 | 65 | P01 Basic | P01.31 | Skip frequency 2 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
43 | P01 Ramps | P01.23 | Skip Frequency 3 Upper Limit |  |  | R/W | 0 | 66 | P01 Basic | P01.32 | Skip frequency 3 (upper limit) | 0.00-599.00 Hz |  | R/W | 0
44 | P01 Ramps | P01.24 | Skip Frequency 3 Lower Limit |  |  | R/W | 0 | 67 | P01 Basic | P01.33 | Skip frequency 3 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
45 | P01 Ramps | P01.25 | DC Injection Current Level | 0~100% |  | ♦R/W | 0 | 353 | P07 Special | P07.01 | DC brake current level | 0-100% |  | ♦R/W | 0
46 | P01 Ramps | P01.26 | DC Injection Time During Start-up | 0.0~60.0 sec |  | ♦R/W | 0 | 354 | P07 Special | P07.02 | DC brake time at start-up | 0.0-60.0 sec. |  | ♦R/W | 0
47 | P01 Ramps | P01.27 | DC Injection Time During Stopping |  |  | ♦R/W | 0 | 355 | P07 Special | P07.03 | DC brake time at STOP | 0.0-60.0 sec. |  | ♦R/W | 0
48 | P01 Ramps | P01.28 | Start-Point for DC Injection During Stopping | 0.00~600.00 Hz |  | ♦R/W | 0 | 356 | P07 Special | P07.04 | DC brake frequency at STOP | 0.00-599.00 Hz |  | ♦R/W | 0
49 | P01 Ramps | P01.29 | Deceleration Method | 0: Normal Ramp Deceleration 1: Over Fluxing Deceleration 2: Traction Energy Control |  | R/W | 0 | 80 | P01 Basic | P01.49 | Regenerative energy restriction control (decel method) | 0: Disable 1: Over voltage energy restriction 2: Traction energy control (TEC) |  | R/W | 0
50 | P02 V/Hz | P02.00 | Volts/Hertz Settings | 0: General Purpose 1: High Starting Torque (TQR) 2: Fans and Pumps 3: Custom 4: 1.5 Power Curve 5: Square Curve |  | R/W | 200 | 77 | P01 Basic P13 Macro/User | P01.43 or P13.00 | V/F curve selection ----------------------- Industry-specific parameter application | 0: V/F curve determined by P01.00-P01.08 1: V/F curve to the power of 1.5 2: V/F curve to the power of 2 ----------------------------------------- 01: User-defined parameter 02: Compressor 03: Fan 04: Pump 05: Conveyor 06: Machine tool 07: Packing 08: Textiles 10: Logistics 11: Tension PID 12: Tension PID + master / auxiliary frequency
51 | P02 V/Hz | P02.01 | Slip Compensation Gain | 0.00~10.00 |  | ♦R/W | 201 | 378 | P07 Special | P07.27 | Slip compensation gain (V/F and SVC control mode) | 0.00-10.00 |  | ♦R/W | 0.00 (Default value is 1.00 in SVC mode)
52 | P02 V/Hz | P02.02 | Torque Compensation Gain | 0~10 |  | ♦R/W | 202 | 377 | P07 Special | P07.26 | Torque compensation gain (V/F and SVC control mode) | IM: 0-10 (when P05.33 = 0) PM: 0-5000 (when P05.33 = 1 or 2) |  | ♦R/W | 1
53 | P02 V/Hz | P02.03 | Torque Compensation Filter | 0.001~10.000 sec |  | ♦R/W | 203 | 375 | P07 Special | P07.24 | Torque command filter time (V/F and SVC control mode) | 0.001-10.000 sec. |  | ♦R/W | 0.05
54 | P02 V/Hz | P02.04 | Motor 1 Middle Output Frequency 1 | 0.00~600.00 Hz |  | R/W | 204 | 37 | P01 Basic | P01.03 | Motor 1, Mid-point frequency 1 | 0.00-599.00 Hz |  | R/W | 3
55 | P02 V/Hz | P02.05 | Motor 1 Middle Output Voltage 1 | 230V: 0.0~240.0V 460V: 0.0~480.0V |  | ♦R/W | 205 | 38 | P01 Basic | P01.04 | Motor 1, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 11.0 22.0 40.0
56 | P02 V/Hz | P02.06 | Motor 1 Middle Output Frequency 2 | 0.00~600.00 Hz |  | R/W | 206 | 39 | P01 Basic | P01.05 | Motor 1, Mid-point frequency 2 | 0.00-599.00 Hz |  | R/W | 1.5
57 | P02 V/Hz | P02.07 | Motor 1 Middle Output Voltage 2 | 230V: 0.0~240.0V 460V: 0.0~480.0V |  | ♦R/W | 207 | 40 | P01 Basic | P01.06 | Motor 1, Mid-point voltage 2 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 5.0 10.0 26.1
58 | P02 V/Hz | P02.08 | Motor 1 Minimum Output Frequency | 0.00~599.99 Hz |  | R/W | 208 | 41 | P01 Basic | P01.07 | Motor 1, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
59 | P02 V/Hz | P02.09 | Motor 1 Minimum Output Voltage | 230V: 0.0~240.0V 460V: 0.0~480.0V |  | ♦R/W | 209 | 42 | P01 Basic | P01.08 | Motor 1, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 1.0 2.0 16.7
60 | P02 V/Hz | P02.10 | PWM Carrier Frequency NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS. | 2~15 kHz |  | R/W | 020A | 14 | P00 Drive | P00.17 | Carrier frequency | Variable Torque: 2-15 kHz Constant Torque: 2-15 kHz Note: When P00-11=5 (IMFOC Sensorless), the maximum setting value for the carrier frequency is 10 kHz. |  | R/W | 4
61 | P02 V/Hz | P02.11 | Control Mode | 0: V/Hz Open Loop Control 1: SVC Sensorless |  | ♦R/W | 020B | 12 | P00 Drive | P00.10 P00.11 | Torque mode Speed (Velocity) Control mode | 0: Speed Control mode 2: Torque mode ---------- 0: IMVF (V/F control) 1: IMVFPG (V/F control + encoder) 2: IM/PM SVC (IM or PM space vector control) 5: IMFOC Sensorless (field-oriented sensorless vector control) Note: For option 2 (SVC), see P05.33 for induction motor (IM) or permanent magnent (PM) motor selection. |  | R/W | 0
62 | P02 V/Hz | P02.12 | Motor 2 Middle Output Frequency 1 | 0.00~600.00 Hz |  | R/W | 020C | 71 | P01 Basic | P01.37 | Motor 2, Mid-point frequency | 0.00-599.00 Hz |  | R/W | 3
63 | P02 V/Hz | P02.13 | Motor 2 Middle Output Voltage 1 | 230V: 0.0~240.0V 460V: 0.0~480.0V |  | ♦R/W | 020D | 72 | P01 Basic | P01.38 | Motor 2, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 11.0 22.0 40.0
64 | P02 V/Hz | P02.14 | Motor 2 Middle Output Frequency 2 | 0.00~600.00 Hz |  | R/W | 020E | 73 | P01 Basic | P01.39 | Motor 2, Mid-point frequency 2 | 0.00-599.00 Hz |  | R/W | 1.5
65 | P02 V/Hz | P02.15 | Motor 2 Middle Output Voltage 2 | 230V: 0.0~240.0V 460V: 0.0~480.0V |  | ♦R/W | 020F | 74 | P01 Basic | P01.40 | Motor 2, Mid-point voltage 2 | 120V / 230V models: 0.0-240.0 V 460V models:0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 5.0 10.0 26.1
66 | P02 V/Hz | P02.16 | Motor 2 Minimum Output Frequency | 0.00~599.99 Hz |  | R/W | 210 | 75 | P01 Basic | P01.41 | Motor 2, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
67 | P02 V/Hz | P02.17 | Motor 2 Minimum Output Voltage | 230V: 0.0~240.0V 460V: 0.0~480.0V |  | ♦R/W | 211 | 76 | P01 Basic | P01.42 | Motor 2, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 1.0 2.0 16.7
68 | P02 V/Hz | P02.18 | Zero Speed Select | 0: Standby 1: Zero Hold 2: Fmin (Min Hz Output) |  | R/W | 212 | 68 | P01 Basic | P01.34 | Zero-speed mode | 0: Output waiting 1: Zero-speed operation 2: Fmin (refer to P01.07 and P01.41) |  | R/W | 0
69 | P02 V/Hz | P02.19 | Start Frequency | 0.00~600.00 Hz |  | R/W | 213 | 43 | P01 Basic | P01.09 | Start-up frequency | 0.00-599.00 Hz |  | R/W | 0.5
70 | P02 V/Hz | P02.20 | Y-D Switching Frequency | 0.00~600.00 Hz |  | ♦R/W | 214 | 244 | P05 Motor | P05.23 | Frequency for Y-connection / fl-connection switch for an induction motor | 0.00-599.00 Hz |  | ♦R/W | 60
71 | P02 V/Hz | P02.21 | Y-D Switching Enable | 0: Disable 1: Enable |  | R/W | 215 | 245 | P05 Motor | P05.24 | Y-connection /fl-connection switch for an induction motor | 0: Disable 1: Enable |  | R/W | 0
72 | P02 V/Hz | P02.22 | Delay Time for Y-D Switching | 0.000~600.000 sec |  | ♦R/W | 216 | 246 | P05 Motor | P05.25 | Delay time for Y-connection /fl-connection switch for an induction motor | 0.000-60.000 sec. |  | ♦R/W | 0.2
73 | P02 V/Hz | P02.23 | Automatic Energy-Saving Operation | 0: Disable 1: Enable |  | ♦R/W | 217 | 372 | P07 Special | P07.21 | Automatic energy- saving setting | 0: Disable 1: Enable |  | ♦R/W | 0
74 | P02 V/Hz | P02.24 | Power Saving Gain | 10~1000% |  | ♦R/W | 218 | 373 | P07 Special | P07.22 | Energy-saving gain | 10-1000% |  | ♦R/W | 100
75 | P02 V/Hz | P02.25 | Slip Compensation Filter | 0.001~10.000 sec |  | ♦R/W | 219 | 376 | P07 Special | P07.25 | Slip compensation filter time (V/F and SVC control mode) | 0.001-10.000 sec. |  | ♦R/W | 0.1
76 | P02 V/Hz | P02.26 | Slip Deviation Level | 0.0~100.0 |  | ♦R/W | 021A | 379 | P07 Special | P07.29 | Slip deviation level | 0.0-100.0% 0: No detection |  | ♦R/W | 0
77 | P02 V/Hz | P02.27 | Slip Deviation Detection time | 0.0~10.0 |  | ♦R/W | 021B | 380 | P07 Special | P07.30 | Over-slip deviation detection time | 0.0-10.0 sec. |  | ♦R/W | 1
78 | P02 V/Hz | P02.28 | Slip Deviation Treatment | 0: Warn and continue OP 1: Warn and Ramp to Stop 2: Warn and Coast to stop 3: No Warn |  | ♦R/W | 021C | 381 | P07 Special | P07.31 | Over-slip deviation treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning |  | ♦R/W | 0
79 | P02 V/Hz | P02.29 | Hunting Gain | 0~10000 |  | ♦R/W | 021D | 382 | P07 Special | P07.32 | Motor oscillation compensation factor | 0-10000 |  | ♦R/W | 1000
80 | P03 Digital | P03.00 | 1st Source of Operation Command [Remote] | 0: Digital Keypad 1: External Terminal; Keypad/RS-485 STOP is enabled 2: External Terminal; Keypad/RS-485 STOP is disabled 3: RS485 (Modbus/BACnet); Keypad STOP is enabled 4: RS485 (Modbus/BACnet); Keypad STOP is disabled 5: Comm Card; Keypad STOP is enabled 6: Comm Card; Keypad STOP is disabled |  | R/W | 0 | 17 | P00 Drive | P00.21 | Operation command source (AUTO, REMOTE) | 0: Digital keypad 1: External terminals 2: RS-485 communication input 3: Not used 5: Communication card Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function settings 41/42 or 56 or with GS4-KPD (optional) |  | ♦R/W | 0
81 | P03 Digital | P03.01 | 2nd Source of Operation Command [Local] |  |  | R/W | 0 | 27 | P00 Drive | P00.31 | Operation command source (HAND, LOCAL) | 0: Digital keypad 1: External terminal 2: RS-485 communication input 3: Not used 5: Communication card Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0
82 | P03 Digital | P03.02 | 2/3 Wire Operation Mode | 0: 2-wire mode 1 (Fwd, Rev) 1: 2-wire mode 2 (Run, Direction) 2: 3-wire mode |  | R/W | 0 | 101 | P02 Digital IO | P02.00 | Two-wire / three- wire operation control | Note: On the drive, DI1 is labeled FWD, and DI2 is labeled REV. 0: No function 1: Two-wire mode 1, power on for operation control (DI1: FWD/STOP, DI2: REV/STOP) 2: Two-wire mode 2, power on for operation control (DI1: RUN/STOP, DI2: REV/FWD) 3: Three-wire, power on for operation control (DI1: RUN, DI2: REV/FWD, DI3: STOP) 4: Two-wire mode 1, Quick Start (DI1: FWD/STOP, DI2: REV/STOP) 5: Two-wire mode 2, Quick Start (DI1: RUN/STOP, DI2: REV/FWD) 6: Three-wire, Quick Start (DI1: RUN, DI2: REV/FWD, DI3: STOP) IMPORTANT 1) In the QuickStart function, terminal output remains in ready status, and the drive responds to the start command immediately. 2) When using the Quick Start function, output terminals U, V, and W are powered immediately. To avoid electric shock hazard, do not touch the terminals or modify the motor wiring. |  | R/W | 1
83 | P03 Digital | P03.03 | Multi-Function Input (DI1) | 0: No function 1: Multi-Speed/PID Multi-Setpoint bit 1 2: Multi-Speed/PID Multi-Setpoint bit 2 3: Multi-Speed/PID Multi-Setpoint bit 3 4: Multi-Speed bit 4 5: Reset 6: JOG 7: Accel/Decel speed inhibit (Speed Hold) 8: 1st~4th Accel/Decel time selection, bit 0 9: 1st~4th Accel/Decel time selection, bit 1 10: External Fault Input by P3.56 (EF error) 11: Base Block Input 12: reserved 13: Disable Auto Accel/Decel Time 14: Switch between drive settings 1 and 2 15: Operation speed command from AI1 16: Operation speed command from AI2 17: Operation speed command from AI3 18: Forced Ramp Stop by P3.56 (no error) 19: Digital Freq Up Command 20: Digital Freq Down Command 21: PID function Disable 22: Clear counter 23: Increment counter value (DI6 only) 24: FWD JOG 25: REV JOG 26: Emergency Stop EF1 (Coast stop)(EF1 error) 27: Signal Confirmation for Y-connection 28: Signal Confirmation for Delta connection 29: Disable EEPROM Write 30: Forced Coast Stop 31: Hand Contact for HOA Control 32: Auto Contact for HOA Control 33: LOCAL/REMOTE Selection 34: Drive Enable 35: Decel Energy Backup (DEB) Enable 36: PLC Mode select bit0 37: PLC Mode select bit1 38: Output MCR Auxiliary Confirmation 39: reserved 40: Fire mode and force drive run 41: Fire mode and maintain operation 42: Disable all motors 43: Disable Motor #1 44: Disable Motor #2 45: Disable Motor #3 46: Disable Motor #4 47: Disable Motor #5 48: Disable Motor #6 49: Disable Motor #7 50: Disable Motor #8 |  | R/W | 1 | 102 | P02 Digital IO | P02.01 | Multi-function input command 1 (FWD/DI1) | 0: No function 1: Multi-step speed command 1 / multi-step position command 1 2: Multi-step speed command 2 / multi-step position command 2 3: Multi-step speed command 3 / multi-step position command 3 4: Multi-step speed command 4 / multi-step position command 4 5: Reset 6: JOG [by external control or GS4- KPD (optional)] 7: Acceleration / deceleration speed inhibit 8: 1st and 2nd acceleration / deceleration time selection 9: 3rd and 4th acceleration / deceleration time selection 10: External Fault (EF) Input (P07.20) 11: Base Block (B.B.) input from external source 12: Output stop 13: Cancel the setting of auto- acceleration / auto-deceleration time 15: Rotating speed command from AI1 16: Rotating speed command from AI2 18: Force to stop (P07.20) 19: Digital up command 20: Digital down command 21: PID function disabled 22: Clear the counter 23: Input the counter value (DI6) 24: FWD JOG command 25: REV JOG command 26: TQC / Field Oriented Control (FOC) mode selection 27: ASR1 / ASR2 selection 28: Emergency stop (EF1) 29: Signal confirmation for Y-connection 30: Signal confirmation for ti. -connection 31: High torque bias (P11.30) 32: Middle torque bias (P11.31) 33: Low torque bias (P11.32) 38: Disable writing EEPROM function 39: Torque command direction 40: Force coasting to stop 41: HAND switch 42: AUTO switch 48: Mechanical gear ratio switch 49: Enable drive | 50: Slave dEb action to execute 51: Selection for PLC mode bit 0 52: Selection for PLC mode bit 1 56: Local / Remote selection 58: Enable fire mode (with RUN command) 59: Enable fire mode (without RUN command) 70: Force auxiliary frequency return to 0 71: Disable PID function, force PID output return to 0 72: Disable PID function, retain the output value before disabled 73: Force PID integral gain return to 0, disable integral 74: Reverse PID feedback 81: Simple positioning zero point position signal input 82: OOB loading balance detection 83: Multi-motor (IM) selection bit 0 84: Multi-motor (IM) selection bit 1 | R/W | 0
84 | P03 Digital | P03.04 | Multi-Function Input (DI2) |  |  | R/W | 2 | 103 | P02 Digital IO | P02.02 | Multi-function input command 2 (REV/DI2) | See P02.01 for values. |  | R/W | 0
85 | P03 Digital | P03.05 | Multi-Function Input (DI3) |  |  | R/W | 3 | 104 | P02 Digital IO | P02.03 | Multi-function input command 3 (DI3) | See P02.01 for values. |  | R/W | 1
86 | P03 Digital | P03.06 | Multi-Function Input (DI4) |  |  | R/W | 4 | 105 | P02 Digital IO | P02.04 | Multi-function input command 4 (DI4) | See P02.01 for values. |  | R/W | 2
87 | P03 Digital | P03.07 | Multi-Function Input (DI5) |  |  | R/W | 0 | 106 | P02 Digital IO | P02.05 | Multi-function input command 5 (DI5) | See P02.01 for values. |  | R/W | 3
88 | P03 Digital | P03.08 | Multi-Function Input (DI6) |  |  | R/W | 0 | 107 | P02 Digital IO | P02.06 | Multi-function input command 6 (DI6) | See P02.01 for values. |  | R/W | 4
89 | P03 Digital | P03.09 | Multi-Function Input (DI7) |  |  | R/W | 0 | 108 | P02 Digital IO | P02.07 | Multi-function input command 7 (DI7) | See P02.01 for values. For pulse input, use selection 0 - No function. |  | R/W | 0
90 | P03 Digital | P03.10 | Multi-Function Input (DI8) |  |  | R/W | 0 | 1000 |  | xN/A
91 | P03 Digital | P03.11 | Multi-Function Input (option card DI10 or PLC X12) |  |  | R/W | 0 | 1001 |  | xN/A
92 | P03 Digital | P03.12 | Multi-Function Input (option card DI11 or PLC X13) |  |  | R/W | 0 | 1002 |  | xN/A
93 | P03 Digital | P03.13 | Multi-Function Input (option card DI12 or PLC X14) |  |  | R/W | 0 | 1003 |  | xN/A
94 | P03 Digital | P03.14 | Multi-Function Input (option card DI13 or PLC X15) |  |  | R/W | 0 | 1004 |  | xN/A
95 | P03 Digital | P03.15 | Multi-Function Input (option card DI14 or PLC X16) |  |  | R/W | 0 | 1005 |  | xN/A
96 | P03 Digital | P03.16 | Multi-Function Input (option card DI15 or PLC X17) |  |  | R/W | 0 | 1006 |  | xN/A
97 | P03 Digital | P03.17 | Multi-Function Output Terminal 1 (Relay 1 or PLC Y0) | 0: no function 1: AC Drive Running 2: At Frequency Setpoint 3: At Speed 1 (P3.32) 4: At Speed 2 (P3.34) 5: At Zero Speed Including Drive Running 6: At Zero Speed Drive not Running 7: Over Torque Level 1 8: Over Torque Level 2 9: Drive Ready 10: Low Voltage warning (Lv) 11: Error indication (All faults, Except for Lv Stop) 12: Brake Release Function (P3.51) 13: Over-temp Warning 14: Dynamic Braking Output 15: PID deviation error 16: Over Slip (oSL) 17: Middle Count Value Attained (P3.45) 18: Final Count Value Attained (P3.44) 19: Base Block Indication 20: Warning Output 21: Overvoltage Alarm 22: Oc Stall Alarm 23: Ov Stall Alarm 24: External Control Mode 25: Forward Command 26: Reverse Command 27: Above Current Output (� P3.52) 28: Below Current Output (< P3.52) 29: Wye Connected Command | 30: Delta Connected Command 31: Zero Speed at Drive Running 32: Zero Speed including Drive Stop 33: Fault Option 1 (P11.00) 34: Fault Option 2 (P11.01) 35: Fault Option 3 (P11.02) 36: Fault Option 4 (P11.03) 37: At Speed (Setpoint include 0Hz) 38: reserved 39: Under Ampere (Low Current) 40: UVW Motor Contactor Enable 41: DEB active 42: Brake Released at Stop 43: RS485 Digital Output 44: Comm Card Digital Output 45: Fire Mode Indication 46: Fire Bypass Indication 47: Motor #1 Selected 48: Motor #2 Selected 49: Motor #3 Selected 50: Motor #4 Selected 51: Motor #5 Selected 52: Motor #6 Selected 53: Motor #7 Selected 54: Motor #8 Selected 55: Mtr1/Mtr2 Nameplate Parameters Select 56: Safety N.O. STO A 57: Safety N.C. STO B 58: Above Frequency Output (� P3.53) 59: Below Frequency Output (< P3.53) | ♦R/W | 11 | 113 | P02 Digital IO | P02.13 | Multi-function output 1 (R1) | 0: No function 1: Indication during RUN 2: Operation speed reached 3: Desired frequency reached 1 (P02.22) 4: Desired frequency reached 2 (P02.24) 5: Zero speed (Frequency command) 6: Zero speed including STOP (Frequency command) 7: Over-torque 1 (P06.06-06.08) 8: Over-torque 2 (P06.09-06.11) 9: Drive is ready 10: Low voltage warning (Lv) (P06.00) 11: Malfunction indication 13: Overheat warning (P06.15) 14: Software brake signal indicator (P07.00) 15: PID feedback error (P08.13, P08.14) 16: Slip error (oSL) 17: Count value reached, does not return to 0 (P02.20) 18: Count value reached, return to 0 (P02.19) 19: External interrupt B.B. input (Base Block) 20: Warning output 21: Over-voltage 22: Over-current stall prevention 23: Over-voltage stall prevention 24: Operation mode 25: Forward command 26: Reverse command 29: Output when frequency � P02.34 30: Output when frequency < P02.34 31: Y-connection for the motor coil 32: t.-connection for the motor coil 33: Zero speed (actual output frequency) 34: Zero speed including STOP (actual output frequency) 35: Error output selection 1 (P06.23) 36: Error output selection 2 (P06.24) 37: Error output selection 3 (P06.25) 38: Error output selection 4 (P06.26) 40: Speed reached (including STOP) 42: Crane function 43: Motor speed detection 44: Low current output (use with P06.71-06.73) 45: UVW output electromagnetic valve switch 46: Master dEb output | 51: Analog output control for RS-485 interface 52: Output control for communication cards 53: Fire mode indication 66: SO output logic A 67: Analog input level reached 68: SO output logic B 73: Over-torque 3 74: Over-torque 4 75: Forward RUN status 76: Reverse RUN status | ♦R/W | 11
98 | P03 Digital | P03.18 | Multi-Function Output Terminal 2 (Relay 2 or PLC Y1) |  |  | ♦R/W | 1 | 1007 |  | xN/A
99 | P03 Digital | P03.19 | Multi-Function Output Terminal 3 (DO1 or PLC Y3) |  |  | ♦R/W | 0 | 114 | P02 Digital IO | P02.16 | Multi-function output 2 (DO1) | See P02.13 for values. |  | ♦R/W | 0
100 | P03 Digital | P03.20 | Multi-Function Output Terminal 4 (DO2 or PLC Y4) |  |  | ♦R/W | 0 | 115 | P02 Digital IO | P02.17 | Multi-function output 3 (DO2) | See P02.13 for values. |  | ♦R/W | 0
101 | P03 Digital | P03.21 | Multi-Function Output Terminal 5 (option card DO10 or RO10, or PLC Y5) |  |  | ♦R/W | 0 | 1008 |  | xN/A
102 | P03 Digital | P03.22 | Multi-Function Output Terminal 6 (option card DO11 or RO11, or PLC Y6) |  |  | ♦R/W | 0 | 1009 |  | xN/A
103 | P03 Digital | P03.23 | Multi-Function Output Terminal 7 (option card RO12 or PLC Y7) |  |  | ♦R/W | 0 | 1010 |  | xN/A
104 | P03 Digital | P03.24 | Multi-Function Output Terminal 8 (option card RO13 or PLC Y10) |  |  | ♦R/W | 0 | 1011 |  | xN/A
105 | P03 Digital | P03.25 | Multi-Function Output Terminal 9 (option card RO14 or PLC Y11) |  |  | ♦R/W | 0 | 1012 |  | xN/A
106 | P03 Digital | P03.26 | Multi-Function Output Terminal 10 (option card RO15 or PLC Y12) |  |  | ♦R/W | 0 | 1013 |  | xN/A
107 | P03 Digital | P03.27 | Multi-Function Virtual Output 11 (DO16, PLC Y13) |  |  | ♦R/W | 0 | 1014 |  | xN/A
108 | P03 Digital | P03.28 | Multi-Function Virtual Output 12 (DO17, PLC Y14) |  |  | ♦R/W | 0 | 1015 |  | xN/A
109 | P03 Digital | P03.29 | Multi-Function Virtual Output 13 (DO18, PLC Y15) |  |  | ♦R/W | 0 | 1016 |  | xN/A
110 | P03 Digital | P03.30 | Multi-Function Virtual Output 14 (DO19, PLC Y16) |  |  | ♦R/W | 0 | 1017 |  | xN/A
111 | P03 Digital | P03.31 | Multi-Function Virtual Output 15 (DO20, PLC Y17) |  |  | ♦R/W | 0 | 1018 |  | xN/A
112 | P03 Digital | P03.32 | Desired Frequency 1 | 0.00~600.00 Hz |  | ♦R/W | 60 | 120 | P02 Digital IO | P02.22 | Desired frequency reached 1 | 0.00-599.00 Hz |  | ♦R/W | 60.00 / 50.00
113 | P03 Digital | P03.33 | Desired Frequency 1 Width | 0.00~600.00 Hz |  | ♦R/W | 2 | 121 | P02 Digital IO | P02.23 | The bandwidth of the desired frequency reached 1 | 0.00-599.00 Hz |  | ♦R/W | 2
114 | P03 Digital | P03.34 | Desired Frequency 2 | 0.00~600.00 Hz |  | ♦R/W | 60 | 122 | P02 Digital IO | P02.24 | Desired frequency reached 2 | 0.00-599.00 Hz |  | ♦R/W | 60.00 / 50.00
115 | P03 Digital | P03.35 | Desired Frequency 2 Width | 0.00~600.00 Hz |  | ♦R/W | 2 | 123 | P02 Digital IO | P02.25 | The bandwidth of the desired frequency reached 2 | 0.00-599.00 Hz |  | ♦R/W | 2
116 | P03 Digital | P03.36 | PID Deviation Level | 1.0~50.0% |  | ♦R/W | 10 | 408 | P08 Hi Func PID | P08.13 | PID feedback signal error deviation level | 1.0-50.0% |  | ♦R/W | 10
117 | P03 Digital | P03.37 | PID Deviation Time | 0.1~300.0 sec |  | ♦R/W | 5 | 409 | P08 Hi Func PID | P08.14 | PID feedback signal error deviation detection time | 0.1-300.0 sec. |  | ♦R/W | 5
118 | P03 Digital | P03.38 | Frequency Output (FO) Scaling Factor | 1~166 |  | ♦R/W | 1 | 119 | P02 Digital IO | P02.21 | Digital output gain (DO) | 1-55 |  | ♦R/W | 1
119 | P03 Digital | P03.39 | Increase/Decrease Speed Mode | 0.000: Following Accel/Decel Time 0.001~1.000 Hz/ms: Following Constant Speed |  | ♦R/W | 0 | 109 | P02 Digital IO | P02.09 | UP / DOWN key mode | 0: UP / DOWN by the acceleration / deceleration time 1: UP / DOWN constant speed (P02.10) 2: Pulse signal (P02.10) 3: External terminals UP / DOWN mode |  | ♦R/W | 0
120 | P03 Digital | P03.40 | DI6 Counter Debounce Filter | 0.00~30.00 sec |  | ♦R/W | 0.02 | 110 | P02 Digital IO | P02.10 | Constant speed, acceleration / deceleration speed of the UP/DOWN Key | 0.001-1.000 Hz/ms |  | ♦R/W | 0.001
121 | P03 Digital | P03.41 | Digital Input Response Time | 0~30.000 sec |  | ♦R/W | 0.005 | 111 | P02 Digital IO | P02.11 | Multi-function input response time | 0.000-30.000 sec. |  | ♦R/W | 0.005
122 | P03 Digital | P03.42 | Multi-Function Input Contact Selection (0=N.O. / 1=N.C.) | 0~65535 0~65535 |  | R/W | 0 | 112 | P02 Digital IO | P02.12 | Multi-function input mode selection | 0000h-FFFFh (0: N.O.; 1: N.C.) |  | ♦R/W | 0
123 | P03 Digital | P03.43 | Multi-Function Output Contact Selection (0=N.O. / 1=N.C.) |  |  | ♦R/W | 0 | 116 | P02 Digital IO | P02.18 | Multi-function output direction ACT | 0000h-FFFFh (0: N.O.; 1: N.C.) |  | ♦R/W | 0000h
124 | P03 Digital | P03.44 | Final Counter Value | 0~65500 |  | ♦R/W | 0 | 117 | P02 Digital IO | P02.19 | Terminal counting value reached (returns to 0) | 0-65500 |  | ♦R/W | 0
125 | P03 Digital | P03.45 | Mid-point Counter Value | 0~65500 |  | ♦R/W | 0 | 118 | P02 Digital IO | P02.20 | Preliminary (Middle) counting value reached (does not return to 0) | 0-65500 |  | ♦R/W | 0
126 | P03 Digital | P03.46 | Digital Input Active Status | 0~65535 |  | Read | 0 | 127 | P02 Digital IO | P02.50 | Display the status of multi-function input terminals DI1-DI7 | Monitor the status of multi-function input terminals |  | Read | 0
127 | P03 Digital | P03.47 | Digital Output Active Status | 0~65535 |  | Read | 0 | 128 | P02 Digital IO | P02.51 | Display the status of multi-function output terminals R1, DO1, DO2 | Monitor the status of digital output terminals |  | Read | 0
128 | P03 Digital | P03.48 | PLC – Digital Input Mask | 0~65535 |  | Read | 0 | 129 | P02 Digital IO | P02.52 | Display the external multi-function input terminals DI1-DI7 used by PLC | Monitor the status of PLC input terminals |  | Read | 0
129 | P03 Digital | P03.49 | PLC – Digital Output Mask | 0~65535 |  | Read | 0 | 130 | P02 Digital IO | P02.53 | Display the external multi-function output terminals R1, DO1, DO2 used by PLC | Monitor the status of PLC output terminals |  | Read | 0
130 | P03 Digital | P03.50 | Increase/Decrease Speed Command Record | 0~600.00 |  | Read | 60 | 131 | P02 Digital IO | P02.54 | Display the frequency command executed by external terminal (EXT Speed REC) | 0.00-599.00 Hz (Read only) |  | Read | 0
131 | P03 Digital | P03.51 | Brake Delay Time | 0.000~65.000 sec |  | R/W | 0 | 324 | P06 Protection | P06.48 | DC brake time for output phase loss | 0.000-65.535 sec. |  | ♦R/W | 0
132 | P03 Digital | P03.52 | Desired Current | 0~150% of GS4 VT current rating |  | ♦R/W | 0 | 1019 |  | xN/A | Use PLC to duplicate function
133 | P03 Digital | P03.53 | Output Frequency Threshold for Multi- Function Output Terminals | 0.00~600.00 Hz |  | ♦R/W | 0 | 124 | P02 Digital IO | P02.34 | Output frequency setting for digital output terminal | 0.00-599.00 Hz (Motor speed when using PG Card) |  | ♦R/W | 0
134 | P03 Digital | P03.54 | reserved | n/a |  | n/a | n/a | 1020 |  | xN/A
135 | P03 Digital | P03.55 | reserved | n/a |  | n/a | n/a | 1021 |  | xN/A
136 | P03 Digital | P03.56 | Emergency Stop (EF) & Force Stop Selection | 0: Coast Stop 1: Deceleration Time 1 2: Deceleration Time 2 3: Deceleration Time 3 4: Deceleration Time 4 5: System Deceleration 6: Automatic Deceleration |  | R/W | 0 | 371 | P07 Special | P07.20 | Emergency stop (EF) & force to stop selection | 0: Coast to stop 1: Stop by the first deceleration time 2: Stop by the second deceleration time 3: Stop by the third deceleration time 4: Stop by the fourth deceleration time 5: System deceleration 6: Automatic deceleration |  | ♦R/W | 0
137 | P03 Digital | P03.57 | AUTO to HAND Switching Behavior | 0~Fh bit 0: Sleep function control bit bit 1: Parameter units displayed on keypad bit 2: PID control bit bit 3: Source of frequency control bit |  | ♦R/W | 0 | 1022 |  | xN/A
138 | P03 Digital | P03.58 | Local/Remote Switch Mode | 0: HAND/OFF/AUTO control 1: Always Stop When Switching 2: Follow Remote Mode 3: Follow Local Mode 4: Follow Local and Remote Mode |  | R/W | 4 | 25 | P00 Drive | P00.29 | LOCAL / REMOTE selection | 0: Standard HOA function 1: When switching between local and remote, the drive stops. 2: When switching between local and remote, the drive runs with REMOTE settings for frequency and operating status. 3: When switching between local and remote, the drive runs with LOCAL settings for frequency and operating status. 4: When switching between local and remote, the drive runs with LOCAL settings when switched to Local and runs with REMOTE settings when switched to Remote for frequency and operating status. |  | R/W | 4
139 | P04 Analog | P04.00 | 1st Source of Frequency Command [Remote] | 0: Digital Keypad 1: RS485 Communication (Modbus/BACnet) 2: Analog Input 3: External UP/DOWN Terminal 4: Comm Card |  | ♦R/W | 0 | 16 | P00 Drive | P00.20 | Master frequency command source (AUTO, REMOTE) | 0: Digital keypad 1: RS-485 communication input 2: External analog input (Refer to P03.00) 3: External UP / DOWN terminal (digital input terminals) 4: Pulse input (DI7) without direction command (refer to P10.16 for pulse input config) 6: Not used 7: Digital keypad VR/potentiometer dial (GS20 only) 8: Communication card 9: PID controller Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0
140 | P04 Analog | P04.01 | 2nd Source of Frequency Command [Local] |  |  | ♦R/W | 0 | 26 | P00 Drive | P00.30 | Master frequency command source (HAND, LOCAL) | 0: Digital keypad 1: RS-485 communication input 2: External analog input (refer to P03.00) 3: External UP / DOWN terminal (digital input terminals) 4: Pulse input without direction command (refer to P10.16 for pulse input config) 6: Not used 7: Digital keypad VR/potentiometer dial (GS20 only) 8: Communication card 9: PID controller Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0
141 | P04 Analog | P04.02 | Analog Input 1 (AI1) Function | 0: no Function 1: Frequency Command/PID Setpoint REMOTE 2: Frequency Command/PID Setpoint LOCAL 3: Frequency Command/PID Setpoint REMOTE & LOCAL 4: reserved 5: PID Feedback Signal 6: PTC Thermistor Input Value 7: PID Setpt Offset 8~10: reserved 11: PT100 RTD Input Value |  | ♦R/W | 1 | 139 | P03 Analog IO | P03.00 | Analog input selection (AI1) | 0: No function 1: Frequency command 2: Torque command (torque limit under speed mode) 3: Torque compensation command 4: PID target value 5: PID feedback signal 6: Thermistor (PTC) input value 7: Positive torque limit 8: Negative torque limit 9: Regenerative torque limit 10: Positive / negative torque limit 11: PT100 thermistor input value 12: Auxiliary frequency input 13: PID compensation value |  | ♦R/W | 1
142 | P04 Analog | P04.03 | Analog Input 2 (AI2) Function |  |  | ♦R/W | 0 | 140 | P03 Analog IO | P03.01 | Analog input selection (AI2) |  |  | ♦R/W | 0
143 | P04 Analog | P04.04 | Analog Input 3 (AI3) Function |  |  | ♦R/W | 0 | 1023 |  | xN/A
144 | P04 Analog | P04.05 | AI1 – I/V Selection | 0: AI_v Selection (0~10V) 1: AI_i Selection (4~20mA) 2: AI_i Selection (0~20mA) |  | ♦R/W | 0 | 156 | P03 Analog IO | P03.28 | AI1 terminal input selection | 0: 0-10 V (only P03.63-P03.68 are valid) 3: -10-10 V (only P03.63-P03.74 are valid) |  | ♦R/W | 0
145 | P04 Analog | P04.06 | AI2 – I/V Selection |  |  | ♦R/W | 1 | 157 | P03 Analog IO | P03.29 | AI2 terminal input selection | 0: 4-20 mA 1: 0-10 V 2: 0-20 mA |  | ♦R/W | 0
146 | P04 Analog | P04.07 | Trim Reference Frequency | 0.00~600.00 Hz |  | R/W | 0 | 1024 |  | xN/A
147 | P04 Analog | P04.08 | Trim Selection | 0: Disable Trim Function 1: 1st Source Freq + 2nd Source Freq 2: 1st Source Freq - 2nd Source Freq 3: Speed Source + Trim Ref Freq 4: Speed Source - Trim Ref Freq |  | R/W | 0 | 1025 |  | xN/A
148 | P04 Analog | P04.09 | Analog Frequency Command for Reverse Run | 0: Negative Frequency Input is Disabled. Forward and reverse directions are controlled by digital keypad or by external terminal. 1: Negative Frequency Input is Enabled. Forward direction when positive frequency; reverse direction when negative frequency. Forward and reverse directions are NOT controlled by digital keypad or by external terminal. |  | ♦R/W | 0 | 145 | P03 Analog IO | P03.10 | Reverse setting when analog signal input is negative frequency | 0: Negative frequency input is not allowed. The digital keypad or external terminal controls the forward and reverse direction. 1: Negative frequency input is allowed. Positive frequency = run in a forward direction; negative frequency = run in a reverse direction. The digital keypad or external terminal control cannot change the running direction. |  | ♦R/W | 0
149 | P04 Analog | P04.10 | AI1 Input Bias (Offset) | -100.0% to +100.0% |  | ♦R/W | 0 | 141 | P03 Analog IO | P03.03 | Analog input bias (AI1) | -100.0-100.0% |  | ♦R/W | 0
150 | P04 Analog | P04.11 | AI1 Input Bias (Offset) Polarity | 0: NO Offset 1: Positive Offset 2: Negative Offset |  | ♦R/W | 0 | 143 | P03 Analog IO | P03.07 | Positive / negative bias mode (AI1) | 0: No bias 1: Lower than or equal to bias 2: Greater than or equal to bias 3: The absolute value of the bias voltage while serving as the center 4: Bias serves as the center |  | ♦R/W | 0
151 | P04 Analog | P04.12 | AI1 Input Gain | -500.0% to +500.0% |  | ♦R/W | 100 | 146 | P03 Analog IO | P03.11 | Analog input gain (AI1) | -500.0-500.0% |  | ♦R/W | 100
152 | P04 Analog | P04.13 | AI1 Filter | 0.00~20.00 sec |  | ♦R/W | 0.01 | 148 | P03 Analog IO | P03.15 | Analog input filter (LPF) time (AI1) | 0.00-20.00 sec. |  | ♦R/W | 0.01
153 | P04 Analog | P04.14 | reserved | n/a |  | n/a | n/a | 1026 |  | xN/A
154 | P04 Analog | P04.15 | AI2 Input Bias (Offset) | -100.0% to +100.0% |  | ♦R/W | 0 | 142 | P03 Analog IO | P03.04 | Analog input bias (AI2) | -100.0-100.0% |  | ♦R/W | 0
155 | P04 Analog | P04.16 | AI2 Input Bias (Offset) Polarity | 0: NO Offset 1: Positive Offset 2: Negative Offset |  | R/W | 0 | 144 | P03 Analog IO | P03.08 | Positive / negative bias mode (AI2) |  |  | ♦R/W | 0
156 | P04 Analog | P04.17 | AI2 Input Gain | -500.0% to +500.0% |  | ♦R/W | 100 | 147 | P03 Analog IO | P03.12 | Analog input gain (AI2) | -500.0-500.0% |  | ♦R/W | 100
157 | P04 Analog | P04.18 | AI2 Filter | 0.00~20.00 sec |  | ♦R/W | 0.01 | 149 | P03 Analog IO | P03.16 | Analog input filter (LPF) time (AI2) | 0.00-20.00 sec. |  | ♦R/W | 0.01
158 | P04 Analog | P04.19 | AI3 Input Bias (Offset) | -100.0% to +100.0% |  | ♦R/W | 0 | 1027 |  | xN/A
159 | P04 Analog | P04.20 | AI3 Input Bias (Offset) Polarity | 0: NO Offset 1: Positive Offset 2: Negative Offset |  | R/W | 0 | 1028 |  | xN/A
160 | P04 Analog | P04.21 | +AI3 Input Gain | -500.0% to +500.0% |  | ♦R/W | 100 | 1029 |  | xN/A
161 | P04 Analog | P04.22 | -AI3 Input Gain | -500.0% to +500.0% |  | ♦R/W | 100 | 1030 |  | xN/A
162 | P04 Analog | P04.23 | AI3 Filter | 0.00~20.00 sec |  | ♦R/W | 0.01 | 1031 |  | xN/A
163 | P04 Analog | P04.24 | AI V/Hz Calculated Selection | 0: All Inputs Use Bias and Gain 1: AI1 Custom V/Hz 2: AI2 Custom V/Hz 3: AI1 and AI2 Custom V/Hz 4: AI3 Custom V/Hz 5: AI1 & AI3 Custom V/Hz 6: AI2 & AI3 Custom V/Hz 7: All Custom V/Hz |  | R/W | 0 | 170 | P03 Analog IO | P03.50 | Analog input curve calculation selection | 0: Normal curve 1: Three-point curve of AI1 2: Three-point curve of AI2 3: Three-point curve of AI1 & AI2 |  | ♦R/W | 0
164 | P04 Analog | P04.25 | AI1 Low V/A | P4.05=0: 0.00~10.00V P4.05=1: 4.00~20.00mA P4.05=2: 0.00~20.00mA |  | R/W | P4.05=0: 0.00V P4.05=1: 4.00mA P4.05=2: 0.00mA | 177 | P03 Analog IO | P03.63 | AI1 voltage lowest point | 0.00-10.00 V |  | ♦R/W | 0
165 | P04 Analog | P04.26 | AI1 Low Hz Percent | 0.00~100.00% |  | R/W | 0 | 178 | P03 Analog IO | P03.64 | AI1 proportional lowest point | -100.00-100.00% |  | ♦R/W | 0
166 | P04 Analog | P04.27 | AI1 Mid V/A | P4.05=0: 0.00~10.00V P4.05=1: 4.00~20.00mA P4.05=2: 0.00~20.00mA |  | R/W | P4.05=0: 5.00V P4.05=1: 12.00mA P4.05=2: 10.00mA | 179 | P03 Analog IO | P03.65 | AI1 voltage mid-point | 0.00-10.00 V |  | ♦R/W | 5
167 | P04 Analog | P04.28 | AI1 Mid Hz Percent | 0.00~100.00% |  | R/W | 50 | 180 | P03 Analog IO | P03.66 | AI1 proportional mid- point | -100.00-100.00% |  | ♦R/W | 50
168 | P04 Analog | P04.29 | AI1 High V/A | P4.05=0: 0.00~10.00V P4.05=1: 4.00~20.00mA P4.05=2: 0.00~20.00mA |  | R/W | P4.05=0: 10.00V P4.05=1: 20.00mA P4.05=2: 20.00mA | 181 | P03 Analog IO | P03.67 | AI1 voltage highest point | 0.00-10.00 V |  | ♦R/W | 10
169 | P04 Analog | P04.30 | AI1 High Hz Percent | 0.00~100.00% |  | R/W | 100 | 182 | P03 Analog IO | P03.68 | AI1 proportional highest point | -100.00-100.00% |  | ♦R/W | 100
170 | P04 Analog | P04.31 | AI2 Low V/A | P4.06=0: 0.00~10.00V P4.06=1: 4.00~20.00mA P4.06=2: 0.00~20.00mA |  | R/W | P4.06=0: 0.00V P4.06=1: 4.00mA P4.06=2: 0.00mA | 171 | P03 Analog IO | P03.57 | AI2 lowest point | P03.29 = 1, 0.00-10.00 V P03.29 t 1, 0.00-20.00 mA |  | ♦R/W | 4
171 | P04 Analog | P04.32 | AI2 Low Hz Percent | 0.00~100.00% |  | R/W | 0 | 172 | P03 Analog IO | P03.58 | AI2 proportional lowest point | 0.00-100.00% |  | ♦R/W | 0
172 | P04 Analog | P04.33 | AI2 Mid V/A | P4.06=0: 0.00~10.00V P4.06=1: 4.00~20.00mA P4.06=2: 0.00~20.00mA |  | R/W | P4.06=0: 5.00V P4.06=1: 12.00mA P4.06=2: 10.00mA | 173 | P03 Analog IO | P03.59 | AI2 mid-point | P03.29 = 1, 0.00-10.00 V P03.29 t 1, 0.00-20.00 mA |  | ♦R/W | 12
173 | P04 Analog | P04.34 | AI2 Mid Hz Percent | 0.00~100.00% |  | R/W | 50 | 174 | P03 Analog IO | P03.60 | AI2 proportional mid- point | 0.00-100.00% |  | ♦R/W | 50
174 | P04 Analog | P04.35 | AI2 High V/A | P4.06=0: 0.00~10.00V P4.06=1: 4.00~20.00mA P4.06=2: 0.00~20.00mA |  | R/W | P4.06=0: 10.00V P4.06=1: 20.00mA P4.06=2: 20.00mA | 175 | P03 Analog IO | P03.61 | AI2 highest point | P03.29 = 1, 0.00-10.00 V P03.29 t 1, 0.00-20.00 mA |  | ♦R/W | 20
175 | P04 Analog | P04.36 | AI2 High Hz Percent | 0.00~100.00% |  | R/W | 100 | 176 | P03 Analog IO | P03.62 | AI2 proportional highest point | 0.00-100.00% |  | ♦R/W | 100
176 | P04 Analog | P04.37 | AI3 Low Voltage Unipolar | 0.00~10.00V |  | R/W | 0 | 1031 |  | xN/A
177 | P04 Analog | P04.38 | AI3 Low Hz Percent Unipolar | 0.00~100.00% |  | R/W | 0 | 1032 |  | xN/A
178 | P04 Analog | P04.39 | AI3 Mid Voltage Unipolar | 0.00~10.00V |  | R/W | 5 | 1033 |  | xN/A
179 | P04 Analog | P04.40 | AI3 Mid Hz Percent Unipolar | 0.00~100.00% |  | R/W | 50 | 1034 |  | xN/A
180 | P04 Analog | P04.41 | AI3 High Voltage Unipolar | 0.00~10.00V |  | R/W | 10 | 1035 |  | xN/A
181 | P04 Analog | P04.42 | AI3 High Hz Percent Unipolar | 0.00~100.00% |  | R/W | 100 | 1036 |  | xN/A
182 | P04 Analog | P04.43 | -AI3 High Voltage Bipolar | -10.00V to 0.00V |  | R/W | 0 | 183 | P03 Analog IO | P03.69- AI1 only | Negative AI1 voltage highest point | -10.00-0.00 V (valid when P03.28 sets as -10-10 V) |  | ♦R/W | 0
183 | P04 Analog | P04.44 | -AI3 High Hz Percent Bipolar | -100.00% to +100.00% |  | R/W | 0 | 184 | P03 Analog IO | P03.69- AI1 only | Negative AI1 proportional highest point | -100.00-100.00% (valid when P03.28 sets as -10-10 V) |  | ♦R/W | 0
184 | P04 Analog | P04.45 | -AI3 Mid Voltage Bipolar | -10.00V to 0.00V |  | R/W | –5.00 | 185 | P03 Analog IO | P03.69- AI1 only | Negative AI1 voltage mid-point | -10.00-0.00 V (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -5
185 | P04 Analog | P04.46 | -AI3 Mid Hz Percent Bipolar | -100.00% to +100.00% |  | R/W | –50.00 | 186 | P03 Analog IO | P03.69- AI1 only | Negative AI1 proportional mid-point | -100.00-100.00% (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -50
186 | P04 Analog | P04.47 | -AI3 Low Voltage Bipolar | -10.00V to 0.00V |  | R/W | –10.00 | 187 | P03 Analog IO | P03.69- AI1 only | Negative AI1 voltage lowest point | -10.00-0.00 V (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -10
187 | P04 Analog | P04.48 | -AI3 Low Hz Percent Bipolar | -100.00% to +100.00% |  | R/W | –100.00 | 188 | P03 Analog IO | P03.69- AI1 only | Negative AI1 proportional lowest point | -100.00-100.00% (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -100
188 | P04 Analog | P04.49 | reserved | n/a |  | n/a | n/a | 1037 |  | xN/A
189 | P04 Analog | P04.50 | Analog Output 1 (AO1) | 0: Output Frequency (Hz) 1: Frequency Command (Hz) 2: Motor Speed (Hz) 3: Output Current (Arms) 4: Output Voltage (V) 5: DC Bus Voltage (V) 6: Power Factor (%) 7: Power (% Rated) 8: AI1 (%) 9: AI2 (%) 10: AI3 (%) 11: As 485 AO 12: As COMM Card AO 13: Fixed Voltage |  | ♦R/W | 0 | 152 | P03 Analog IO | P03.20 | Multi-function output (A01) | 0: Output frequency (Hz) 1: Frequency command (Hz) 2: Motor speed (Hz) 3: Output current (rms) 4: Output voltage 5: DC bus voltage 6: Power factor 7: Power 8: Output torque 9: AI1 10: AI2 12: Iq current command 13: Iq feedback value 14: Id current command 15: Id feedback value 16: Vq-axis voltage command 17: Vd-axis voltage command 18: Torque command 19: PG2 (DI7) frequency command 21: RS-485 analog output 22: Communication card analog output 23: Constant voltage output |  | ♦R/W | 0
190 | P04 Analog | P04.51 | AO1 Gain | 0.0~500.0% |  | ♦R/W | 100 | 153 | P03 Analog IO | P03.21 | Analog output gain (A01) | 0.0-500.0% |  | ♦R/W | 100
191 | P04 Analog | P04.52 | AO1 Negative Value Handle | 0: Absolute Value 1: 0V When Negative 2: Offset 5V = 0 Value |  | ♦R/W | 0 | 154 | P03 Analog IO | P03.22 | Analog output in REV direction (A01) | 0: Absolute value in output voltage 1: Reverse output 0 V; forward output 0-10 V 2: Reverse output 5-0 V; forward output 5-10 V |  | ♦R/W | 0
192 | P04 Analog | P04.53 | AO1 0~20mA/4~20mA Selection | 0: 0~20mA 1: 4~20mA |  | R/W | 0 | 159 | P03 Analog IO | P03.31 | A01 output selection | 0: 0-10 V output 1: 0-20 mA output 2: 4-20 mA output |  | ♦R/W | 0
193 | P04 Analog | P04.54 | Analog Output 2 (AO2) | 0: Output Frequency (Hz) 1: Frequency Command (Hz) 2: Motor Speed (Hz) 3: Output Current (Arms) 4: Output Voltage (V) 5: DC Bus Voltage (V) 6: Power Factor (%) 7: Power (% Rated) 8: AI1 (%) 9: AI2 (%) 10: AI3 (%) 11: As 485 AO 12: As COMM Card AO 13: Fixed Voltage |  | ♦R/W | 0 | 1037 |  | xN/A
194 | P04 Analog | P04.55 | AO2 Gain | 0.0~500.0% |  | ♦R/W | 100 | 1038 |  | xN/A
195 | P04 Analog | P04.56 | AO2 Negative Value Handle | 0: Absolute Value 1: 0V When Negative 2: Offset 5V = 0 Value |  | ♦R/W | 0 | 1039 |  | xN/A
196 | P04 Analog | P04.57 | AO2 0~20mA/4~20mA Selection | 0: 0~20mA 1: 4~20mA |  | R/W | 0 | 1040 |  | xN/A
197 | P04 Analog | P04.58 | reserved | n/a |  | n/a | n/a | 1038 |  | xN/A
198 | P04 Analog | P04.59 | AO2 Offset (Bias) | -100.00% to +100.00% |  | ♦R/W | 0 | 1039 |  | xN/A
199 | P04 Analog | P04.60 | AO1 Output Constant Level | 0.00~100.00% |  | R/W | 0 | 160 | P03 Analog IO | P03.32 | A01 DC output setting level | 0.00-100.00% |  | ♦R/W | 0
200 | P04 Analog | P04.61 | AO2 Output Constant Level | 0.00~100.00% |  | R/W | 0 | 1041 |  | xN/A
201 | P04 Analog | P04.62 | PLC Analog Output Mask | 0 to 65535 |  | ♦R/W | 0 | 158 | P03 Analog IO | P03.30 | PLC analog output terminal status | Monitor the status of the PLC analog output terminals bit 0: A01 status |  | Read | 0
202 | P04 Analog | P04.63 | Loss of AI1 Signal (4~20mA) | 0: Disable 1: Run at Last Freq (ANL Warning) 2: Decelerate to 0Hz (ANL Warning) 3: Stop (ACE Fault) |  | R/W | 0 | 1041 |  | xN/A
203 | P04 Analog | P04.64 | Loss of AI2 Signal (4~20mA) |  |  |  | 0 | 151 | P03 Analog IO | P03.19 | Signal loss selection for analog input 4-20 mA | 0: Disable 1: Continue operation at the last frequency 2: Decelerate to 0 Hz 3: Stop immediately and display "ACE" |  | ♦R/W | 0
204 | P05 Presets | P05.00 | Jog Frequency | 0.00~600.00 Hz |  | ♦R/W |  | 56 | P01 Basic | P01.22 | JOG frequency | 0.00-599.00 Hz |  | ♦R/W | 6
205 | P05 Presets | P05.01 | Multi-Speed 1 | 0.00~600.00 Hz |  | ♦R/W |  | 189 | P04 Multi Step Spd | P04.00 | 1st step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
206 | P05 Presets | P05.02 | Multi-Speed 2 | 0.00~600.00 Hz |  | ♦R/W |  | 190 | P04 Multi Step Spd | P04.01 | 2nd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
207 | P05 Presets | P05.03 | Multi-Speed 3 | 0.00~600.00 Hz |  | ♦R/W |  | 191 | P04 Multi Step Spd | P04.02 | 3rd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
208 | P05 Presets | P05.04 | Multi-Speed 4 | 0.00~600.00 Hz |  | ♦R/W |  | 192 | P04 Multi Step Spd | P04.03 | 4th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
209 | P05 Presets | P05.05 | Multi-Speed 5 | 0.00~600.00 Hz |  | ♦R/W |  | 193 | P04 Multi Step Spd | P04.04 | 5th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
210 | P05 Presets | P05.06 | Multi-Speed 6 | 0.00~600.00 Hz |  | ♦R/W |  | 194 | P04 Multi Step Spd | P04.05 | 6th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
211 | P05 Presets | P05.07 | Multi-Speed 7 | 0.00~600.00 Hz |  | ♦R/W |  | 195 | P04 Multi Step Spd | P04.06 | 7th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
212 | P05 Presets | P05.08 | Multi-Speed 8 | 0.00~600.00 Hz |  | ♦R/W |  | 196 | P04 Multi Step Spd | P04.07 | 8th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
213 | P05 Presets | P05.09 | Multi-Speed 9 | 0.00~600.00 Hz |  | ♦R/W |  | 197 | P04 Multi Step Spd | P04.08 | 9th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
214 | P05 Presets | P05.10 | Multi-Speed 10 | 0.00~600.00 Hz |  | ♦R/W |  | 198 | P04 Multi Step Spd | P04.09 | 10th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
215 | P05 Presets | P05.11 | Multi-Speed 11 | 0.00~600.00 Hz |  | ♦R/W |  | 199 | P04 Multi Step Spd | P04.10 | 11th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
216 | P05 Presets | P05.12 | Multi-Speed 12 | 0.00~600.00 Hz |  | ♦R/W |  | 200 | P04 Multi Step Spd | P04.11 | 12th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
217 | P05 Presets | P05.13 | Multi-Speed 13 | 0.00~600.00 Hz |  | ♦R/W |  | 201 | P04 Multi Step Spd | P04.12 | 13th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
218 | P05 Presets | P05.14 | Multi-Speed 14 | 0.00~600.00 Hz |  | ♦R/W |  | 202 | P04 Multi Step Spd | P04.13 | 14th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
219 | P05 Presets | P05.15 | Multi-Speed 15 | 0.00~600.00 Hz |  | ♦R/W |  | 203 | P04 Multi Step Spd | P04.14 | 15th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
220 | P06 Protection | P06.00 | Electronic Thermal Overload Relay (Motor 1) NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS. | 0: Constant Torque 1: Variable Torque 2: Inactive |  | ♦R/W | 1 | 290 | P06 Protection | P06.13 | Electronic thermal relay selection 1 (motor 1) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with fan on the shaft) 2: Disabled |  | ♦R/W | 2
221 | P06 Protection | P06.01 | Electronic Thermal Characteristic (Motor 1) | 30.0~600.0 sec |  | ♦R/W | 60 | 291 | P06 Protection | P06.14 | Electronic thermal relay action time 1 (motor 1) | 30.0-600.0 sec. |  | ♦R/W | 60
222 | P06 Protection | P06.02 | Electronic Thermal Overload Relay (Motor 2) NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS. | 0: Constant Torque 1: Variable Torque 2: Inactive |  | ♦R/W | 2 | 305 | P06 Protection | P06.27 | Electronic thermal relay selection 2 (motor 2) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with fan on the shaft) 2: Disabled |  | ♦R/W | 2
223 | P06 Protection | P06.03 | Electronic Thermal Characteristic (Motor 2) | 30.0~600.0 sec |  | ♦R/W | 60 | 306 | P06 Protection | P06.28 | Electronic thermal relay action time 2 (motor 2) | 30.0-600.0 sec. |  | ♦R/W | 60
224 | P06 Protection | P06.04 | Auto Restart after Fault | 0~10 |  | ♦R/W | 0 | 363 | P07 Special | P07.11 | Number of times of restart after fault | 0-10 |  | ♦R/W | 0
225 | P06 Protection | P06.05 | Reset Time for Auto Restart after fault | 0.0~6000.0 sec |  | ♦R/W | 60 | 383 | P07 Special | P07.33 | Auto-restart interval of fault | 0.0-6000.0 sec. |  | ♦R/W | 60
226 | P06 Protection | P06.06 | Base Block Speed Search after Fault (oc,ov,bb) | 0: Disable 1: Speed search starts with current speed reference 2: Speed search starts with minimum output frequency |  | ♦R/W | 0 | 362 | P07 Special | P07.10 | Restart after fault action | 0: Stop operation 1: Speed tracking by current speed 2: Speed tracking by minimum output frequency |  | ♦R/W | 0
227 | P06 Protection | P06.07 | Speed Search at Start | 0: Disable 1: Speed search from maximum output frequency 2: Speed search from start-up motor frequency 3: Speed search from minimum output frequency |  | ♦R/W | 0 | 364 | P07 Special | P07.12 | Speed tracking during start-up | 0: Disable 1: Speed tracking by the maximum output frequency 2: Speed tracking by the motor frequency at start-up 3: Speed tracking by the minimum output frequency |  | ♦R/W | 0
228 | P06 Protection | P06.08 | Momentary Power Loss | 0: Disable 1: Speed search for last frequency command 2: Speed search for the minimum output frequency |  | ♦R/W | 0 | 358 | P07 Special | P07.06 | Restart after momentary power loss | 0: Stop operation 1: Speed tracking by the speed before the power loss 2: Speed tracking by the minimum output frequency |  | ♦R/W | 0
229 | P06 Protection | P06.09 | Fwd/Rev Direction Inhibit | 0: Enable Fwd/Rev 1: Disable Reverse Operation 2: Disable Forward Operation |  | ♦R/W | 0 | 19 | P00 Drive | P00.23 | Motor direction control | 0: Enable forward / reverse 1: Disable reverse 2: Disable forward |  | ♦R/W | 0
230 | P06 Protection | P06.10 | Auto Voltage Regulation | 0: AVR Enable 1: AVR Disable 2: AVR Disable during Decel |  | ♦R/W | 0 | 374 | P07 Special | P07.23 | Automatic voltage regulation (AVR) function | 0: Enable AVR 1: Disable AVR 2: Disable AVR during deceleration |  | ♦R/W | 0
231 | P06 Protection | P06.11 | Over-Voltage Stall Prevention | 0: Enable Over-voltage Stall Prevention 1: Disable Over-voltage Stall Prevention |  | R/W | 0 | 276 | P06 Protection | P06.01 | Over-voltage stall prevention | 0: Disable 120V / 230V models: 0.0-390.0 VDC 460V models: 0.0-900.0 VDC 575V models: 0.0-1000.0 VDC |  | ♦R/W | 380.0 760.0 975.0
232 | P06 Protection | P06.12 | Selection for Over- voltage Stall Prevention | 0: Traditional Over-voltage Stall Prevention 1: Advanced Over-voltage Prevention |  | ♦R/W | 0 | 277 | P06 Protection | P06.02 | Selection for over-voltage stall prevention | 0: Traditional over-voltage stall prevention 1: Smart over-voltage stall prevention |  | ♦R/W | 0
233 | P06 Protection | P06.13 | Auto Adjustable Accel/ Decel | 0: Linear Accel/Decel 1: Auto Accel, Linear Decel 2: Linear Accel, Auto Decel 3: Auto Accel, Auto Decel 4: Auto Accel/Decel Stall Prevention (limited by P1.01~P1.08 and P1.13~P1.14) |  | ♦R/W | 0 | 78 | P01 Basic | P01.44 | Auto-acceleration and auto-deceleration setting | 0: Linear acceleration and deceleration 1: Auto-acceleration and linear deceleration 2: Linear acceleration and auto- deceleration 3: Auto-acceleration and auto- deceleration 4: Stall prevention by auto- acceleration and auto-deceleration (limited by P01.12 -P01.21) |  | ♦R/W | 0
234 | P06 Protection | P06.14 | Over-Torque Detection Mode (OT1) | 0: Disable 1: Enable during at speed 2: Enable during at speed and Stop 3: Enable during OP 4: Enable during OP and Stop |  | ♦R/W | 0 | 283 | P06 Protection | P06.06 | Over-torque detection selection (motor 1) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN |  | ♦R/W | 0
235 | P06 Protection | P06.15 | Over-Torque Detection Level (OT1) | 10~200% |  | ♦R/W | 120 | 284 | P06 Protection | P06.07 | Over-torque detection level (motor 1) | 10-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 120
236 | P06 Protection | P06.16 | Over-Torque Detection Time (OT1) | 0.1~60.0 sec |  | ♦R/W | 0.1 | 285 | P06 Protection | P06.08 | Over-torque detection time (motor 1) | 0.1-60.0 sec. |  | ♦R/W | 0.1
237 | P06 Protection | P06.17 | Over-Torque Detection Mode (OT2) | 0: Disable 1: Enable during at speed 2: Enable during at speed and Stop 3: Enable during OP 4: Enable during OP and Stop |  | ♦R/W | 0 | 286 | P06 Protection | P06.09 | Over-torque detection selection (motor 2) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN |  | ♦R/W | 0
238 | P06 Protection | P06.18 | Over-Torque Detection Level (OT2) | 10~200% |  | ♦R/W | 120 | 287 | P06 Protection | P06.10 | Over-torque detection level (motor 2) | 10-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 120
239 | P06 Protection | P06.19 | Over-Torque Detection Time (OT2) | 0.1~60.0 sec |  | ♦R/W | 0.1 | 288 | P06 Protection | P06.11 | Over-torque detection time (motor 2) | 0.1-60.0 sec. |  | ♦R/W | 0.1
240 | P06 Protection | P06.20 | Over-Current Stall Prevention Level During Accel | 0~160% (by P6.34 setup; VT: 0~130%; CT: 0~160%) 0: Disable |  | ♦R/W | VT: 120 CT: 150 | 279 | P06 Protection | P06.03 | Over-current stall prevention during acceleration (OCA) |  |  | ♦R/W | 180
241 | P06 Protection | P06.21 | Over-Current Stall Prevention Level During Operation | 0~160% (by P6.34 setup; VT: 0~130%; CT: 0~160%) 0: Disable |  | ♦R/W | VT: 120 CT: 150 | 281 | P06 Protection | P06.04 | Over-current stall prevention during operation (OCN) |  |  | ♦R/W | 180
242 | P06 Protection | P06.22 | Maximum Allowable Power Loss Time | 0.0~20.0 sec |  | ♦R/W | 2 | 359 | P07 Special | P07.07 | Allowed power loss duration | 0.0-20.0 sec. |  | ♦R/W | 2
243 | P06 Protection | P06.23 | Base-Block Time for Speed Search | 0.1~20.0 sec |  | ♦R/W | 0.5 | 360 | P07 Special | P07.08 | Base Block time | 0.0-60.0 sec. |  | ♦R/W | 0.5
244 | P06 Protection | P06.24 | Maximum Speed Search Current Level | 20~200% |  | ♦R/W | 100 | 361 | P07 Special | P07.09 | Current limit of speed tracking | 20-200% |  | ♦R/W | 100
245 | P06 Protection | P06.25 | Upper Limit of Output Frequency | 0.00~600.00 Hz |  | ♦R/W | 600 | 44 | P01 Basic | P01.10 | Output frequency upper limit | 0.00-599.00 Hz |  | ♦R/W | 599
246 | P06 Protection | P06.26 | Lower Limit of Output Frequency | 0.00~600.00 Hz |  | ♦R/W | 0 | 45 | P01 Basic | P01.11 | Output frequency lower limit | 0.00-599.00 Hz |  | ♦R/W | 0
247 | P06 Protection | P06.27 | Over-Voltage Stall Prevention Level | 230V: 300.0~450.0 VDC 460V: 600.0~900.0 VDC |  | ♦R/W | 390.0 780.0 | 276 | P06 Protection | P06.01 | Over-voltage stall prevention | 0: Disable 120V / 230V models: 0.0-390.0 VDC 460V models: 0.0-900.0 VDC 575V models: 0.0-1000.0 VDC |  | ♦R/W | 380.0 760.0 975.0
248 | P06 Protection | P06.28 | Dynamic Braking Voltage Level | 230V: 350.0~450.0 VDC 460V: 700.0~900.0 VDC |  | ♦R/W | 390.0 780.0 | 352 | P07 Special | P07.00 | Software brake chopper threshold level | 120V / 230V models: 350.0-450.0 VDC 460V models: 700.0-900.0 VDC 575V models: 875.0-1000.0 VDC |  | ♦R/W | 370.0 740.0 950.0
249 | P06 Protection | P06.29 | Line Start Lockout | 0: Enable start-up lockout 1: Disable start-up lockout |  | ♦R/W | 0 | 125 | P02 Digital IO | P02.35 | External operation control selection after fault reset and reboot | 0: Disable 1: Drive runs if the RUN command remains after reset or reboot |  | ♦R/W | 0
250 | P06 Protection | P06.30 | Heat Sink OH Warning Level | 0.0~110.0 °C |  | ♦R/W | 105 | 292 | P06 Protection | P06.15 | Temperature level overheat (OH) warning | 0.0-110.00C |  | ♦R/W | Model dependent
251 | P06 Protection | P06.31 | Cooling Fan Control | 0: Always ON 1: Fan OFF 1 minute after Stop 2: Run fan ON/Stop fan OFF 3: Heat sink temperature 4: Always OFF |  | ♦R/W | 0 | 370 | P07 Special | P07.19 | Fan cooling control | 0: Fan is always ON 1: Fan is OFF after the AC motor drive stops for one minute. 2: Fan is ON when the AC motor drive runs, fan is OFF when the AC motor drive stops. 3: Fan turns ON when temperature (IGBT) reaches approx 600C. |  | ♦R/W | 3
252 | P06 Protection | P06.32 | PWM Fan Speed | 0~100% |  | R/W | 60 | 1042 |  | xN/A
253 | P06 Protection | P06.33 | Drive Derating Method NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS. | 0: Constant rated current 1: Constant carrier frequency 2: Constant rated current (with higher current limit) |  | R/W | 0 | 327 | P06 Protection | P06.55 | Derating protection | 0: Constant rated current and limit carrier frequency by load current and temperature 1: Constant carrier frequency and limit load current by setting carrier frequency 2: Constant rated current (same as setting 0), but close current limit |  | ♦R/W | 0
254 | P06 Protection | P06.34 | Variable/Constant Torque Duty Selection NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS. | 0: VT, 3-phase input 1: CT, 3-phase input 2: CT, 230V 1-phase input |  | ♦R/W | 0 | 13 | P00 Drive | P00.16 | Torque duty selection | 0: Variable Torque (VT) 1: Constant Torque (CT) |  | R/W | 1
255 | P06 Protection | P06.35 | Low Voltage Level | 230V Frame <E: 150.0~220.0 VDC 230V Frame �E: 190.0~220.0 VDC 460V Frame <E: 300.0~440.0 VDC 460V Frame �E: 380.0~440.0 VDC |  | ♦R/W | 180.0 200.0 360.0 400.0 | 275 | P06 Protection | P06.00 | Low voltage level | 120V / 230V models: 150.0-220.0 VDC 460V models: 300.0-440.0 VDC 575V models: 375.0-550.0 VDC |  | ♦R/W | 180.0 360.0 450.0
256 | P06 Protection | P06.36 | OC Stall Preventation Accel/Decel Time Selection at Normal Speed | 0: Follow System Accel/Decel Time 2: Follow the 2nd Accel/Decel Time 3: Follow the 3rd Accel/Decel Time 4: Follow the 4th Accel/Decel Time 5: Auto Accel/Decel |  | ♦R/W | 0 | 282 | P06 Protection | P06.05 | Acceleration / deceleration time selection for stall prevention at constant speed | 0: By current acceleration / deceleration time 1: By the first acceleration / deceleration time 2: By the second acceleration / deceleration time 3: By the third acceleration / deceleration time 4: By the fourth acceleration / deceleration time 5: By Auto-acceleration / auto- deceleration |  | ♦R/W | 0
257 | P06 Protection | P06.37 | OC Stall Preventation Limit for operation over Rated Speed | 0~100% |  | ♦R/W | 50 | 293 | P06 Protection | P06.16 | Stall prevention limit level (Weak magnetic field current stall prevention level) | 0-100% (refer to P06.03-P06.04) |  | ♦R/W | 100
258 | P06 Protection | P06.38 | Torque Limit (Current Limit) | 0~200% |  | ♦R/W | 150 | 289 | P06 Protection | P06.12 | Current limit | 0-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 150
259 | P06 Protection | P06.39 | PTC/RTD Detection Selection | 0: Warn and Run 1: Warn and Ramp Stop 2: Warn and Coast Stop 3: No Warning |  | ♦R/W | 0 | 307 | P06 Protection | P06.29 | PTC detection selection | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning |  | ♦R/W | 0
260 | P06 Protection | P06.40 | PTC Level | 0.0~100.0% |  | ♦R/W | 50 | 308 | P06 Protection | P06.30 | PTC level | 0.0-100.0% |  | ♦R/W | 50
261 | P06 Protection | P06.41 | RTD (PT100) Level 1, PTC Level Detection Selection | 0.000~10.000V |  | R/W | 5 | 328 | P06 Protection | P06.56 | PT100 voltage level 1 | 0.000-10.000 V |  | ♦R/W | 5
262 | P06 Protection | P06.42 | RTD (PT100) Level 2, PTC Level Detection Selection | 0.000~10.000V |  | R/W | 7 | 329 | P06 Protection | P06.57 | PT100 voltage level 2 | 0.000-10.000 V |  | ♦R/W | 7
263 | P06 Protection | P06.43 | RTD (PT100) Drop Frequency for PT100 Level 1 | 0.00~600.00 Hz |  | R/W | 0 | 330 | P06 Protection | P06.58 | PT100 level 1 frequency protection | 0.00-599.00 Hz |  | ♦R/W | 0
264 | P06 Protection | P06.44 | RTD (PT100) Treatment Delay Time | 0~6000 sec |  | R/W | 60 | 331 | P06 Protection | P06.59 | PT100 activation level 1 protection frequency delay time | 0-6000 sec. |  | ♦R/W | 60
265 | P06 Protection | P06.45 | Output Phase Loss (OPhL) Detection Selection | 0: Warn and continue to operate 1: Warn and ramp to stop 2: Warn and coast to stop 3: No warning |  | R/W | 3 | 321 | P06 Protection | P06.45 | Output phase loss detection action (OPHL) | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning |  | ♦R/W | 3
266 | P06 Protection | P06.46 | Output Phase Loss Detection time | 0.000~65.535 sec |  | R/W | 0.5 | 322 | P06 Protection | P06.46 | Detection time for output phase loss | 0.000-65.535 sec. |  | ♦R/W | 0.5
267 | P06 Protection | P06.47 | Output Phase Loss Current Detection Level | 0.00~100.00% (of max current) |  | R/W | 1 | 323 | P06 Protection | P06.47 | Current detection level for output phase loss | 0.00-100.00% |  | ♦R/W | 1
268 | P06 Protection | P06.48 | Output Phase Loss DCI Time | 0.000~65.535 sec |  | R/W | 0 | 324 | P06 Protection | P06.48 | DC brake time for output phase loss | 0.000-65.535 sec. |  | ♦R/W | 0
269 | P06 Protection | P06.49 | Input Phase Loss Treatment | 0: Warn and ramp to stop 1: Warn and coast to stop |  | R/W | 0 | 326 | P06 Protection | P06.53 | Input phase loss detection action (OrP) | 0: Fault and ramp to stop 1: Fault and coast to stop |  | ♦R/W | 0
270 | P06 Protection | P06.50 | GFF Detect Current Level (% of INV I-Rated) | 0.0~100.0% |  | R/W | 60 | 332 | P06 Protection | P06.60 | Software detection GFF current level | 0.0-6553.5% |  | ♦R/W | 60
271 | P06 Protection | P06.51 | GFF Low Pass Filter Gain | 0.00~655.35 |  | R/W | 0.1 | 333 | P06 Protection | P06.61 | Software detection GFF filter time | 0.00-655.35 sec. |  | ♦R/W | 0.1
272 | P06 Protection | P06.52 | Low Current Level | 0.0~100.0% |  | R/W | 0 | 342 | P06 Protection | P06.71 | Low current setting level | 0.0-100.0% |  | ♦R/W | 0
273 | P06 Protection | P06.53 | Low Current Detection Time | 0.00~360.00 sec |  | R/W | 0 | 343 | P06 Protection | P06.72 | Low current detection time | 0.00-360.00 sec. |  | ♦R/W | 0
274 | P06 Protection | P06.54 | Low Current Action | 0: Disable, no warning 1: Warn and coast to stop 2: Warn and ramp to stop by 2nd decel time 3: Warn and continue operation |  | R/W | 0 | 344 | P06 Protection | P06.73 | Low current action | 0: No function 1: Fault and coast to stop 2: Fault and ramp to stop by the second deceleration time 3: Warn and continue operation |  | ♦R/W | 0
275 | P06 Protection | P06.55 | Fire Mode | 0: Disable 1: Forward Operation 2: Reverse Operation |  | R/W | 0 | 345 | P06 Protection | P06.80 | Fire mode | 0: Disable 1: Operates in a counterclockwise direction 2: Operates in a clockwise direction |  | R/W | 0
276 | P06 Protection | P06.56 | Fire Mode Operation Frequency | 0.00~600.00 Hz |  | R/W | 60 | 346 | P06 Protection | P06.81 | Operating frequency in fire mode | 0.00-599.00 Hz |  | ♦R/W | 60
277 | P06 Protection | P06.57 | Fire Mode Enable Bypass | 0: Disable Bypass 1: Enable Bypass |  | R/W | 0 | 1043 |  | xN/A
278 | P06 Protection | P06.58 | Fire Mode Bypass Delay Time | 0.0~6550.0 sec |  | R/W | 0 | 1044 |  | xN/A
279 | P06 Protection | P06.59 | Fire Mode Auto Restart Counter | 0~10 |  | R/W | 0 | 1045 |  | xN/A
280 | P06 Protection | P06.60 | Fire Mode Auto Restart Counter Reset Time | 0.0~6000.0 sec |  | R/W | 60 | 1046 |  | xN/A
281 | P06 Protection | P06.61 | Decel Energy Backup (DEB) Decel Selection | 0: Disable 1: 1st Decel Time 2: 2nd Decel Time 3: 3rd Decel Time 4: 4th Decel Time 5: Current Decel Time 6: Auto Decel Time |  | ♦R/W | 0 | 365 | P07 Special | P07.13 | dEb function selection | 0: Disable 1: dEb with auto-acceleration / auto- deceleration, the drive does not output the frequency after the power is restored. 2: dEb with auto-acceleration / auto- deceleration, the drive outputs the frequency after the power is restored. 3: dEb low-voltage control, then the drive's voltage increases to 350 VDC / 700 VDC and ramps to stop after low frequency 4: dEb high-voltage control of 350 VDC / 700 VDC, and the drive ramps to stop |  | ♦R/W | 0
282 | P06 Protection | P06.62 | DEB Offset Level | 230V models: 0.0~100.0 VDC 460V models: 0.0~200.0 VDC |  | R/W | 40.0 80.0 | 1047 |  | xN/A
283 | P06 Protection | P06.63 | DEB Disable Voltage Level | 230V models: 0.0~200.0 VDC 460V models: 0.0~400.0 VDC |  | R/W | 150.0 300.0 | 1048 |  | xN/A
284 | P06 Protection | P06.64 | DEB Delay Time | 0.0~25.0 sec |  | ♦R/W | 0 | 1049 |  | xN/A
285 | P06 Protection | P06.65 | Dwell Time at Accel | 0.00~600.00 sec |  | ♦R/W | 0 | 366 | P07 Special | P07.15 | Dwell time at acceleration | 0.00-600.00 sec. |  | ♦R/W | 0
286 | P06 Protection | P06.66 | Dwell Frequency at Accel | 0.00~600.00 Hz |  | ♦R/W | 0 | 367 | P07 Special | P07.16 | Dwell frequency at acceleration | 0.00-599.00 Hz |  | ♦R/W | 0
287 | P06 Protection | P06.67 | Dwell Time at Decel | 0.00~600.00 sec |  | ♦R/W | 0 | 368 | P07 Special | P07.17 | Dwell time at deceleration | 0.00-600.00 sec. |  | ♦R/W | 0
288 | P06 Protection | P06.68 | Dwell Frequency at Decel | 0.00~600.00 Hz |  | ♦R/W | 0 | 369 | P07 Special | P07.18 | Dwell frequency at deceleration | 0.00-599.00 Hz |  | ♦R/W | 0
289 | P06 Protection | P06.69 | Input Phase Loss Detection Time | 0.00~600.00 sec |  | R/W | 0.2 | 322 | P06 Protection | P06.46 | Detection time for output phase loss | 0.000-65.535 sec. |  | ♦R/W | 0.5
290 | P06 Protection | P06.70 | Input Phase Loss Ripple Detection | 230V models: 0.0~160.0 VDC 460V models: 0.0~320.0 VDC |  | R/W | 30.0 60.0 | 323 | P06 Protection | P06.47 | Current detection level for output phase loss | 0.00-100.00% |  | ♦R/W | 1
291 | P06 Protection | P06.71 | STO Alarm Latch | 0: STO Alarm Latch 1: STO Alarm no Latch |  | ♦R/W | 0 | 320 | P06 Protection | P06.44 | STO latch selection | 0: STO latch 1: STO no latch |  | ♦R/W | 0
292 | P07 PID | P07.00 | PID Action/Mode | 0: PID Disabled 1: PID Reverse Local/Remote 2: PID Forward Local/Remote 3: PID Reverse Remote Only 4: PID Forward Remote Only 5: PID Reverse Local Only 6: PID Forward Local Only |  | ♦R/W | 0 | 395 | P08 Hi Func PID | P08.00 | Terminal selection of PID feedback | 0: No function 1: Negative PID feedback: by analog input (P03.00, P03.01) 2: Negative PID feedback: by single- phase input (DI7), without direction (P10.16=5) 4: Positive PID feedback: by analog input (P03.00, P03.01) 5: Positive PID feedback: by single- phase input (DI7), without direction (P10.16=5) 7: Negative PID feedback: by communication protocols 8: Positive PID feedback: by communication protocols |  | ♦R/W | 0
293 | P07 PID | P07.01 | reserved | ~ |  | ~ | ~ | 1060 |  | xN/A
294 | P07 PID | P07.02 | PID Setpoint Source Display (when PID enabled, this parameter data will be mapped from P4.00~P4.01 dependent upon whether in Remote=4.00 or Local=4.01) | 00: Keypad 01: RS485 02: AI1 03: AI2 04: AI3 05: Ext Up/Down Key 06: Comm Card 07: Multi-Step Inputs 08: PID off |  | Read | 7 | 425 | P08 Hi Func PID | P08.65 | PID target value source | 0: Frequency command (P00.20, P00.30) 1: P08.66 setting 2: RS-485 communication input 3: External analog input (refer to P03.00, P03.01) 6: Communication card 7: Digital keypad potentiometer dial (GS20 only) |  | ♦R/W | 0
295 | P07 PID | P07.03 | PID Feedback Gain | 0.00 to 300.00% |  | ♦R/W | 100 | 1061 |  | xN/A
296 | P07 PID | P07.04 | PID Offset Value | -100.0% to +100.0% |  | ♦R/W | 0 | 412 | P08 Hi Func PID | P08.17 | PID compensation | -100.0-100.0% |  | ♦R/W | 0
297 | P07 PID | P07.05 | Keypad PID Setpoint | 0.00~100.00% |  | Read | 0 | 1061 |  | xN/A | use PLC with inputs to duplicate function
298 | P07 PID | P07.06 | PID Multi-Setpoint 1 | 0.00~100.00% |  | ♦R/W | 0 | 1062 |  | xN/A | use PLC with inputs to duplicate function
299 | P07 PID | P07.07 | PID Multi-Setpoint 2 | 0.00~100.00% |  | ♦R/W | 0 | 1063 |  | xN/A | use PLC with inputs to duplicate function
300 | P07 PID | P07.08 | PID Multi-Setpoint 3 | 0.00~100.00% |  | ♦R/W | 0 | 1064 |  | xN/A | use PLC with inputs to duplicate function
301 | P07 PID | P07.09 | PID Multi-Setpoint 4 | 0.00~100.00% |  | ♦R/W | 0 | 1065 |  | xN/A | use PLC with inputs to duplicate function
302 | P07 PID | P07.10 | PID Multi-Setpoint 5 | 0.00~100.00% |  | ♦R/W | 0 | 1066 |  | xN/A | use PLC with inputs to duplicate function
303 | P07 PID | P07.11 | PID Multi-Setpoint 6 | 0.00~100.00% |  | ♦R/W | 0 | 1067 |  | xN/A | use PLC with inputs to duplicate function
304 | P07 PID | P07.12 | PID Multi-Setpoint 7 | 0.00~100.00% |  | ♦R/W | 0 | 1068 |  | xN/A | use PLC with inputs to duplicate function
305 | P07 PID | P07.13 | Proportional Gain | 0.0~100.0 |  | ♦R/W | 1 | 396 | P08 Hi Func PID | P08.01 | Proportional gain (P) | 0.0-1000.0 (When P08.23 bit 1=0) 0.00-100.00 (When P08.23 bit 1=1) |  | ♦R/W | 1
306 | P07 PID | P07.14 | Integral Time | 0.00~100.00 sec |  | ♦R/W | 1 | 397 | P08 Hi Func PID | P08.02 | Integral time (I) | 0.00-100.00 sec. |  | ♦R/W | 1
307 | P07 PID | P07.15 | Derivative Value | 0.00~1.00 sec |  | ♦R/W | 0 | 398 | P08 Hi Func PID | P08.03 | Differential time (D) | 0.00-1.00 sec. |  | ♦R/W | 0
308 | P07 PID | P07.16 | Upper Limit for Integral Time | 0.0~100.0% |  | ♦R/W | 100 | 399 | P08 Hi Func PID | P08.04 | Upper limit of integral control | 0.0-100.0% |  | ♦R/W | 100
309 | P07 PID | P07.17 | Derivative Filter Time Constant | 0.0~2.5 sec |  | ♦R/W | 0 | 402 | P08 Hi Func PID | P08.07 | PID delay time | 0.0-2.5 sec. |  | ♦R/W | 0
310 | P07 PID | P07.18 | PID Output Frequency Limit | 0.0~100.0% |  | ♦R/W | 100 | 400 | P08 Hi Func PID | P08.05 | PID output command limit (positive limit) | 0.0-110.0% |  | ♦R/W | 100
311 | P07 PID | P07.19 | PID Feedback Value | -200.00% to +200.00% |  | Read | 0 | 401 | P08 Hi Func PID | P08.06 | PID feedback value by communication protocol | -200.00-200.00% |  | ♦R/W | 0
312 | P07 PID | P07.20 | Feedback Signal Detection Time | 0.0~3600.0 sec |  | ♦R/W | 0 | 403 | P08 Hi Func PID | P08.08 | Feedback signal detection time | 0.0-3600.0 sec. |  | ♦R/W | 0
313 | P07 PID | P07.21 | PID Feedback Loss | 0: Warn and Continue Operation 1: Warn (fault) and Ramp to Stop 2: Warn (fault) and Coast to Stop 3: Warn and Operate at Last Frequency 4: Warn and Run at P7.22 |  | R/W | 0 | 404 | P08 Hi Func PID | P08.09 | Feedback signal fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: Warn and operate at last frequency |  | ♦R/W | 0
314 | P07 PID | P07.22 | PID Feedback Loss Speed Level Default | 0.00~400.00 Hz |  | ♦R/W | 0 | 1069 |  | xN/A
315 | P07 PID | P07.23 | reserved | ~ |  | ~ | ~ | 1070 |  | xN/A
316 | P07 PID | P07.24 | PID Offset Selection | 0: Set by P7.04 1: Set by an AI Input |  | ♦R/W | 0 | 411 | P08 Hi Func PID | P08.16 | PID compensation selection | 0: Parameter setting 1: Analog input |  | ♦R/W | 0
317 | P07 PID | P07.25 | PID Mode Selection | 0: Old PID mode, Kp, Kp*Ki, Kp*Kd 1: New PID mode, Kp, Ki, Kd are independent |  | R/W | 0 | 415 | P08 Hi Func PID | P08.20 | PID mode selection | 0: Serial connection 1: Parallel connection |  | R/W | 0
318 | P07 PID | P07.26 | PID Reverse Enable | 0: PID can't change command direction 1: PID can change command direction |  | R/W | 0 | 416 | P08 Hi Func PID | P08.21 | Enable PID to change the operation direction | 0: Operation direction cannot be changed 1: Operation direction can be changed |  | R/W | 0
319 | P07 PID | P07.27 | Source of Sleep | 0: Frequency / PID Command Frequency (CV) 1: Feedback |  | R/W | 0 | 413 | P08 Hi Func PID | P08.18 | Sleep mode function setting | 0: Refer to PID output command 1: Refer to PID feedback signal |  | R/W | 0
320 | P07 PID | P07.28 | Integral Limit During Sleep | 0.0~200.0 |  | R/W | 50 | 414 | P08 Hi Func PID | P08.19 | Wake-up integral limit | 0.0-200.0% |  | ♦R/W | 50
321 | P07 PID | P07.29 | Sleep Reference | P7.27=0: 0.0~600.00 Hz P7.27=1: 0.0~200.00% |  | ♦R/W | 0 | 405 | P08 Hi Func PID | P08.10 | Sleep frequency | 0.00-599.00 Hz |  | ♦R/W | 0
322 | P07 PID | P07.30 | Wake-up Reference | P7.27=0: 0.0~600.00 Hz P7.27=1: 0.0~200.00% |  | ♦R/W | 0 | 406 | P08 Hi Func PID | P08.11 | Wake-up frequency | 0.00-599.00 Hz |  | ♦R/W | 0
323 | P07 PID | P07.31 | Sleep Time | 0.0~6000.0 sec |  | ♦R/W | 0 | 407 | P08 Hi Func PID | P08.12 | Sleep time | 0.0-6000.0 sec. |  | ♦R/W | 0
324 | P07 PID | P07.32 | Wake-up Delay Time | 0.00~600.00 sec |  | R/W | 0 | 417 | P08 Hi Func PID | P08.22 | Wake-up delay time | 0.00-600.00 sec. |  | ♦R/W | 0
325 | P08 Display | P08.00 | User Display | 0: Output Amps 1: Counter Value 2: Actual Freq 3: DC Bus Voltage 4: Output Voltage 5: Power Factor 6: Output Power 7: Calculated RPM 8~9: reserved 10: PID Feedback % 11: AI1 % 12: AI2 % 13: AI3 % 14: IGBT Temperature 15: Cap Temperature 16: DI Input Status 17: DO Output Status 18: Multi-Speed Step 19: CPU DI Status 20: CPU DO Status | 21~24: reserved 25: Overload % 26: Ground Fault % 27: DC Bus Ripple 28: PLC D1043 Value 29: reserved 30: User-Defined 31: Out Hz x P8.05 32~33: reserved 34: Fan Speed 35: reserved 36: Carrier Frequency 37: reserved 38: Drive Status 39: reserved 40: reserved 41: kWh 42: PID Reference 43: PID Offset 44: PID Output Hz | ♦ R/W | 3 | 5 | P00 Drive | P00.04 | User Display | 0: Output Amps (A) (unit: Amp) 1: Counter Value (c) (unit: CNT) 2: Output Frequency (H.) (unit: Hz) 3: DC Bus Voltage (V) (unit: VDC) 4: Output Voltage (E) (unit: VAC) 5: Power Factor (n) (unit: deg) 6: Output Power (P) (unit: kW) 7: Calculated RPM (r) (unit: rpm) 8: Est Output Torque (t) (unit: %) 10: PID Feedback (b) (unit: %) 11: AI1 Analog Input Signal (1.) (unit: %) 12: AI2 Analog Input Signal (2.) (unit: %) 14: IGBT Temperature (i.) (unit: 0C) 16: DI Input Status (ON / OFF) (i) 17: DO Output Status (ON / OFF) (o) 18: Multi-Speed Step (S) 19: CPU DI Input Status (d) 20: CPU DO Output Status (0.) 22: Pulse input frequency (S.) 25: Overload count (0.00-100.00%) (o.) (unit: %) 26: Ground fault GFF (G.) (unit: %) 27: DC bus voltage ripple (r.) (unit: VDC) 28: Display PLC register D1043 data (C) 30: Display the output of User-defined (U) 31: Display P00-05 user gain (K) 35: Control mode display 36: Present operating carrier frequency of the drive (J.) (Unit: Hz) 38: Display the drive status (6.) 39: Display the drive's estimated output torque, positive and negative, using N•m as unit (t 0.0: positive torque; -0.0: negative torque) (C.) 40: Torque command (L.) (unit: %) 41: kWh display (J) (unit: kWh) 42: PID target value (h.) (unit: %) 43: PID compensation (o.) (unit: %) 44: PID output frequency (b.) (unit: Hz) 46: Auxiliary frequency value (U.) (unit: Hz) 47: Master frequency value (A) (unit: Hz) 48: Frequency value after addition and subtraction of master and auxiliary frequency (L.) (unit: Hz) 51: PMSVC torque offset 58: P00.05 User gain display (K) (Does not display decimal places.) 62: I2t (o.) (unit: %) 63: Error code (E.) 64: Warning code (n.) 65: Accumulated motor operation record (day) (r.) (refer to P05.32) |  | ♦R/W | 3
326 | P08 Display | P08.01 | Start-up Display Selection | 0: Freq Setpoint 1: Output Hz 2: User Display (P8.00) 3: Output Amps |  | ♦ R/W | 0 | 4 | P00 Drive | P00.03 | Start-up display Selection | 0: F - Freq Setpoint 1: H - Output Hz 2: U - User Display P00-04) 3: A - Output Amps |  | ♦R/W | 0
327 | P08 Display | P08.02 | User Defined Format | Bits 0~3: User defined decimal place: 0000b: no decimal place 0001b: one decimal place 0010b: two decimal place 0011b: three decimal place Bits 4~9: User defined unit: 000xh: Hz 001xh: rpm 002xh: % 003xh: kg 004xh: m/s 005xh: kW 006xh: hp 007xh: ppm 008xh: 1/m 009xh: kg/s 00Axh: kg/m 00Bxh: kg/h 00Cxh: lb/s 00Dxh: lb/m 00Exh: lb/h 00Fxh: ft/s 010xh: ft/m 011xh: m 012xh: ft 013xh: °C 014xh: °F 015xh: mbar 016xh: bar 017xh: Pa 018xh: kPa 019xh: mWG 01Axh: inWG 01Bxh: ftWG 01Cxh: psi 01Dxh: atm 01Exh: L/s 01Fxh: L/m 020xh: L/h 021xh: m3/s 022xh: m3/h 023xh: gpm 024xh: cfm |  | R/W | 0 | 21 | P00 Drive | P00.25 | User-defined characteristics (COEFF ATT) | bit 0-3: user-defined decimal places 0000h-0000b: no decimal place 0001h-0001b: one decimal place 0002h-0010b: two decimal places 0003h-0011b: three decimal places bit 4-5: user-defined unit 000xh: Hz 001xh: rpm 002xh: % 003xh: kg 004xh: m/s 005xh: kW 006xh: HP 007xh: ppm 008xh: 1/m 009xh: kg/s 00Axh: kg/m 00Bxh: kg/h 00Cxh: lb/s 00Dxh: lb/m 00Exh: lb/h 00Fxh: ft/s 010xh: ft/m 011xh: m 012xh: ft 013xh: degC 014xh: degF 015xh: mbar 016xh: bar 017xh: Pa 018xh: kPa 019xh: mWG 01Axh: inWG 01Bxh: ftWG 01Cxh: psi 01Dxh: atm 01Exh: L/s 01Fxh: L/m 020xh: L/h 021xh: m3/s 022xh: m3/h 023xh: GPM 024xh: CFM |  | ♦R/W | 0
329 | P08 Display | P08.03 | User Defined Max | 0: Disable 0~65535 (when P8.02 set to no decimal place) 0.0~6553.5 (when P8.02 set to 1 decimal place) 0.00~655.35 (when P8.02 set to 2 decimal place) 0.000~65.535 (when P8.02 set to 3 decimal place) |  | R/W | 0 | 23 | P00 Drive | P00.26 | User-defined maximum value (COEFF MAX) | 0: Disable 0-65535 (when P00.25 is set to no decimal place) 0.0-6553.5 (when P00.25 is set to one decimal place) 0.00-655.35 (when P00.25 is set to two decimal places) 0.000-65.535 (when P00.25 is set to three decimal places) |  | RW | 0
330 | P08 Display | P08.04 | User Defined Setpoint | 0~65535 |  | Read | 0 | 24 | P00 Drive | P00.27 | User-defined value (COEFF SET) | Read only |  | Read | 0
331 | P08 Display | P08.05 | Output Frequency Gain | 0.00~160.00 |  | R/W | 1 | 7 | P00 Drive | P00.05 | Coefficient Gain in Actual Output Frequency Display (H Page scale) | 0.00-160.00 |  | ♦R/W | 1
332 | P08 Display | P08.06 | Password Input | 0~65535 |  | ♦ R/W | 0 | 9 | P00 Drive | P00.07 | Parameter protection password input | 0-65535 0-4: the number of password attempts allowed |  | ♦R/W | 0
333 | P08 Display | P08.07 | Password Set Up | 0~65535 |  | ♦ R/W | 0 | 10 | P00 Drive | P00.08 | Parameter protection password setting | 0-65535 0: No password protection or password entered correctly (P00-07) 1: Parameter has been set |  | ♦R/W | 0
334 | P08 Display | P08.08 | Power On Counter | 0~65535 |  | Read | ~ | 1080 |  | xN/A
335 | P08 Display | P08.09 | Power On Day | 0~65535 |  | Read | ~ | 1081 |  | xN/A
336 | P08 Display | P08.10 | Power On Minute | 0~1439 |  | Read | ~ | 1082 |  | xN/A
337 | P08 Display | P08.11 | Accumulative Motor Operation Time (minute) | 0~1439 |  | Read | ~ | 252 | P05 Motor | P05.31 | Accumulated motor operation time (Minutes) | 0-1439 |  | R/W | 0
338 | P08 Display | P08.12 | Accumulative Motor Operation Time (day) | 0~65535 |  | Read | ~ | 253 | P05 Motor | P05.32 | Accumulated motor operation time (days) | 0-65535 |  | R/W | 0
339 | P08 Display | P08.13 | Keypad Communication Fault Treatment | 0: Warn & Continue Operation 1: Warn & Ramp to Stop 2: Warn & Coast to Stop 3: No Warning & Continue Operation |  | R/W | 2 | 1083 |  | xN/A
340 | P08 Display | P08.14 | Keypad Time Out | 0.0~100.0 sec |  | R/W | 1 | 1084 |  | xN/A
341 | P08 Display | P08.15 | reserved | ~ |  | ~ | 0 | 1085 |  | xN/A
342 | P08 Display | P08.16 | reserved | ~ |  | ~ | 0 | 1086 |  | xN/A
343 | P08 Display | P08.17 | reserved | ~ |  | ~ | 0 | 1087 |  | xN/A
344 | P08 Display | P08.18 | reserved | ~ |  | ~ | 0 | 1088 |  | xN/A
345 | P08 Display | P08.19 | reserved | ~ |  | ~ | 0 | 1089 |  | xN/A
346 | P08 Display | P08.20 | PLC Buffer 1 | 0~65535 |  | R/W | 0 | 204 | P04 Multi Step Spd | P04.50 | PLC buffer 0 | 0-65535 |  | ♦R/W | 0
347 | P08 Display | P08.21 | PLC Buffer 2 | 0~65535 |  | R/W | 0 | 205 | P04 Multi Step Spd | P04.51 | PLC buffer 1 | 0-65535 |  | ♦R/W | 0
348 | P08 Display | P08.22 | PLC Buffer 3 | 0~65535 |  | R/W | 0 | 206 | P04 Multi Step Spd | P04.52 | PLC buffer 2 | 0-65535 |  | ♦R/W | 0
349 | P08 Display | P08.23 | PLC Buffer 4 | 0~65535 |  | R/W | 0 | 207 | P04 Multi Step Spd | P04.53 | PLC buffer 3 | 0-65535 |  | ♦R/W | 0
350 | P08 Display | P08.24 | PLC Buffer 5 | 0~65535 |  | R/W | 0 | 208 | P04 Multi Step Spd | P04.54 | PLC buffer 4 | 0-65535 |  | ♦R/W | 0
351 | P08 Display | P08.25 | PLC Buffer 6 | 0~65535 |  | R/W | 0 | 209 | P04 Multi Step Spd | P04.55 | PLC buffer 5 | 0-65535 |  | ♦R/W | 0
352 | P08 Display | P08.26 | PLC Buffer 7 | 0~65535 |  | R/W | 0 | 210 | P04 Multi Step Spd | P04.56 | PLC buffer 6 | 0-65535 |  | ♦R/W | 0
353 | P08 Display | P08.27 | PLC Buffer 8 | 0~65535 |  | R/W | 0 | 211 | P04 Multi Step Spd | P04.57 | PLC buffer 7 | 0-65535 |  | ♦R/W | 0
354 | P08 Display | P08.28 | PLC Buffer 9 | 0~65535 |  | R/W | 0 | 212 | P04 Multi Step Spd | P04.58 | PLC buffer 8 | 0-65535 |  | ♦R/W | 0
355 | P08 Display | P08.29 | PLC Buffer 10 | 0~65535 |  | R/W | 0 | 213 | P04 Multi Step Spd | P04.59 | PLC buffer 9 | 0-65535 |  | ♦R/W | 0
356 | P08 Display | P08.30 | PLC Buffer 11 | 0~65535 |  | R/W | 0 | 214 | P04 Multi Step Spd | P04.60 | PLC buffer 10 | 0-65535 |  | ♦R/W | 0
357 | P08 Display | P08.31 | PLC Buffer 12 | 0~65535 |  | R/W | 0 | 215 | P04 Multi Step Spd | P04.61 | PLC buffer 11 | 0-65535 |  | ♦R/W | 0
358 | P08 Display | P08.32 | PLC Buffer 13 | 0~65535 |  | R/W | 0 | 216 | P04 Multi Step Spd | P04.62 | PLC buffer 12 | 0-65535 |  | ♦R/W | 0
359 | P08 Display | P08.33 | PLC Buffer 14 | 0~65535 |  | R/W | 0 | 217 | P04 Multi Step Spd | P04.63 | PLC buffer 13 | 0-65535 |  | ♦R/W | 0
360 | P08 Display | P08.34 | PLC Buffer 15 | 0~65535 |  | R/W | 0 | 218 | P04 Multi Step Spd | P04.64 | PLC buffer 14 | 0-65535 |  | ♦R/W | 0
361 | P08 Display | P08.35 | PLC Buffer 16 | 0~65535 |  | R/W | 0 | 219 | P04 Multi Step Spd | P04.65 | PLC buffer 15 | 0-65535 |  | ♦R/W | 0
362 | P08 Display | P08.36 | PLC Buffer 17 | 0~65535 |  | R/W | 0 | 220 | P04 Multi Step Spd | P04.66 | PLC buffer 16 | 0-65535 |  | ♦R/W | 0
363 | P08 Display | P08.37 | PLC Buffer 18 | 0~65535 |  | R/W | 0 | 221 | P04 Multi Step Spd | P04.67 | PLC buffer 17 | 0-65535 |  | ♦R/W | 0
364 | P08 Display | P08.38 | PLC Buffer 19 | 0~65535 |  | R/W | 0 | 222 | P04 Multi Step Spd | P04.68 | PLC buffer 18 | 0-65535 |  | ♦R/W | 0
365 | P08 Display | P08.39 | PLC Buffer 20 | 0~65535 |  | R/W | 0 | 223 | P04 Multi Step Spd | P04.69 | PLC buffer 19 | 0-65535 |  | ♦R/W | 0
366 | P09 Serial Comm | P09.00 | VFD Comm Address | 1 to 254 |  | ♦ R/W | 1 | 437 | P09 Communication | P09.00 | Communication address | 1-254 |  | ♦R/W | 1
367 | P09 Serial Comm | P09.01 | Modbus Baud Rate | 0: 4.8k 1: 9.6k 2: 19.2k | 3: 38.4k 4: 57.6k 5: 115.2k | ♦ R/W | 1 | 438 | P09 Communication | P09.01 | COM1 transmission speed | 4.8-115.2 Kbps |  | ♦R/W | 9.6
368 | P09 Serial Comm | P09.02 | Modbus Protocol | 1: 7N2 (ASCII) 2: 7E1 (ASCII) 3: 7O1 (ASCII) 4: 7E2 (ASCII) 5: 7O2 (ASCII) 6: 8N1 (ASCII) 7: 8N2 (ASCII) 8: 8E1 (ASCII) 9: 8O1 (ASCII) | 10: 8E2 (ASCII) 11: 8O2 (ASCII) 12: 8N1 (RTU) 13: 8N2 (RTU) 14: 8E1 (RTU) 15: 8O1 (RTU) 16: 8E2 (RTU) 17: 8O2 (RTU) | ♦ R/W | 12 | 441 | P09 Communication | P09.04 | COM1 communication protocol | 1: 7, N, 2 (ASCII) 2: 7, E, 1 (ASCII) 3: 7, O, 1 (ASCII) 4: 7, E, 2 (ASCII) 5: 7, O, 2 (ASCII) 6: 8, N, 1 (ASCII) 7: 8, N, 2 (ASCII) 8: 8, E, 1 (ASCII) 9: 8, O, 1 (ASCII) 10: 8, E, 2 (ASCII) 11: 8, O, 2 (ASCII) 12: 8, N, 1 (RTU) 13: 8, N, 2 (RTU) 14: 8, E, 1 (RTU) 15: 8, O, 1 (RTU) 16: 8, E, 2 (RTU) 17: 8, O, 2 (RTU) |  | ♦R/W | 1
369 | P09 Serial Comm | P09.03 | Modbus Fault Select | 0: Warn & Continue Operation 1: Warn & Ramp to Stop 2: Warn & Coast to Stop 3: No Warning & Continue Operation |  | ♦ R/W | 3 | 439 | P09 Communication | P09.02 | COM1 transmission fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning, no fault, and continue operation |  | ♦R/W | 3
370 | P09 Serial Comm | P09.04 | Modbus Time Out Detection | 0: Disable 1: Enable |  | ♦ R/W | 0 | 440 | P09 Communication | P09.03=0 disable | COM1 time-out detection (set zero for disable) | 0.0-100.0 sec. |  | ♦R/W | 0
371 | P09 Serial Comm | P09.05 | Modbus Time Out Duration | 0.1 to 100.0 seconds |  | ♦ R/W | 0.5 | 440 | P09 Communication | P09.03 | COM1 time-out detection (set zero for disable) | 0.0-100.0 sec. |  | ♦R/W | 0
372 | P09 Serial Comm | P09.06 | Parameter Copy | 0: Disable Copy Keypad Function 1: Enable Copy Keypad Function |  | ♦ R/W | 0 | 1091 |  | xN/A
373 | P09 Serial Comm | P09.07 | Parameter Lock | 0: Normal Operation (allow changes) 1: Prevent any Changes to Parameters |  | R/W | 0 | 3 | P00 Drive | P00.02 | Restore to Default | 0: No function 1: Parameter Lock 2: Convert to GS2 mode (Step 1 of 2) 3: Not used 4: Not used 5: Reset kWh Display to 0 6: Reset PLC 8: Disable Keypad Run 9: Reset all parameters to 50Hz defaults 10: Reset all parameters to 60Hz defaults 11: Reset all parameters to 50Hz defaults (retain user-defined parameter values P13.01~P13.50) 12: Reset all parameters to 60Hz defaults (retain user-defined parameter values P13.01~P13.50) 13: Not used 20: Convert to GS2 mode (Step 2 of 2) |  | R/W | 0
374 | P09 Serial Comm | P09.08 | Restore to Default | 0: no function 1: Parameter Lock 2: no function 3: no function 4: no function 5: Reset kWh Display to Zero 6: Reset PLC (clear PLC) 7: no function 8: no function 9: Reset 50Hz Default 10: Reset 60Hz Default |  | R/W | 0 | 3 | P00 Drive | P00.02 | Restore to Default | 0: No function 1: Parameter Lock 2: Convert to GS2 mode (Step 1 of 2) 3: Not used 4: Not used 5: Reset kWh Display to 0 6: Reset PLC 8: Disable Keypad Run 9: Reset all parameters to 50Hz defaults 10: Reset all parameters to 60Hz defaults 11: Reset all parameters to 50Hz defaults (retain user-defined parameter values P13.01~P13.50) 12: Reset all parameters to 60Hz defaults (retain user-defined parameter values P13.01~P13.50) 13: Not used 20: Convert to GS2 mode (Step 2 of 2) |  | R/W | 0
375 | P09 Serial Comm | P09.09 | Block Transfer Data Location 1 | 0~65535 * P9.09~P9.24 can be set in run mode if the corresponding Block Transfer Address Pointer (P9.69~P9.84) is pointing to a register that allows writes while in run mode. |  | * R/W | 0 | 444 | P09 Communication | P09.11 | Block transfer 1 | 0-65535 |  | ♦R/W | 0
376 | P09 Serial Comm | P09.10 | Block Transfer Data Location 2 |  |  |  |  | 445 | P09 Communication | P09.12 | Block transfer 2 | 0-65535 |  | ♦R/W | 0
377 | P09 Serial Comm | P09.11 | Block Transfer Data Location 3 |  |  |  |  | 446 | P09 Communication | P09.13 | Block transfer 3 | 0-65535 |  | ♦R/W | 0
378 | P09 Serial Comm | P09.12 | Block Transfer Data Location 4 |  |  |  |  | 447 | P09 Communication | P09.14 | Block transfer 4 | 0-65535 |  | ♦R/W | 0
379 | P09 Serial Comm | P09.13 | Block Transfer Data Location 5 |  |  |  |  | 448 | P09 Communication | P09.15 | Block transfer 5 | 0-65535 |  | ♦R/W | 0
380 | P09 Serial Comm | P09.14 | Block Transfer Data Location 6 |  |  |  |  | 449 | P09 Communication | P09.16 | Block transfer 6 | 0-65535 |  | ♦R/W | 0
381 | P09 Serial Comm | P09.15 | Block Transfer Data Location 7 |  |  |  |  | 450 | P09 Communication | P09.17 | Block transfer 7 | 0-65535 |  | ♦R/W | 0
382 | P09 Serial Comm | P09.16 | Block Transfer Data Location 8 |  |  |  |  | 451 | P09 Communication | P09.18 | Block transfer 8 | 0-65535 |  | ♦R/W | 0
383 | P09 Serial Comm | P09.17 | Block Transfer Data Location 9 |  |  |  |  | 452 | P09 Communication | P09.19 | Block transfer 9 | 0-65535 |  | ♦R/W | 0
384 | P09 Serial Comm | P09.18 | Block Transfer Data Location 10 |  |  |  |  | 453 | P09 Communication | P09.20 | Block transfer 10 | 0-65535 |  | ♦R/W | 0
385 | P09 Serial Comm | P09.19 | Block Transfer Data Location 11 |  |  |  |  | 454 | P09 Communication | P09.21 | Block transfer 11 | 0-65535 |  | ♦R/W | 0
386 | P09 Serial Comm | P09.20 | Block Transfer Data Location 12 |  |  |  |  | 455 | P09 Communication | P09.22 | Block transfer 12 | 0-65535 |  | ♦R/W | 0
387 | P09 Serial Comm | P09.21 | Block Transfer Data Location 13 |  |  |  |  | 456 | P09 Communication | P09.23 | Block transfer 13 | 0-65535 |  | ♦R/W | 0
388 | P09 Serial Comm | P09.22 | Block Transfer Data Location 14 |  |  |  |  | 457 | P09 Communication | P09.24 | Block transfer 14 | 0-65535 |  | ♦R/W | 0
389 | P09 Serial Comm | P09.23 | Block Transfer Data Location 15 |  |  |  |  | 458 | P09 Communication | P09.25 | Block transfer 15 | 0-65535 |  | ♦R/W | 0
390 | P09 Serial Comm | P09.24 | Block Transfer Data Location 16 |  |  |  |  | 459 | P09 Communication | P09.26 | Block transfer 16 | 0-65535 |  | ♦R/W | 0
391 | P09 Serial Comm | P09.25 | reserved | n/a |  | n/a | n/a | 1092 |  | xN/A
392 | P09 Serial Comm | P09.26 | RS485 Speed Reference | 0.00~600.00 Hz |  | Read | 60 | 1093 |  | xN/A | use words 2000, 2001, 2002
393 | P09 Serial Comm | P09.27 | RS485 RUN Command | 0: Stop 1: Run |  | ♦ R/W | 0 | 1094 |  | xN/A | use words 2000, 2001, 2003
394 | P09 Serial Comm | P09.28 | RS485 Direction Command | 0: Forward 1: Reverse |  | ♦ R/W | 0 | 1095 |  | xN/A | use words 2000, 2001, 2004
395 | P09 Serial Comm | P09.29 | RS485 External Fault | 0: No Fault 1: External Fault |  | ♦ R/W | 0 | 1096 |  | xN/A | use words 2000, 2001, 2005
396 | P09 Serial Comm | P09.30 | RS485 Fault Reset | 0: No Action 1: Fault Reset |  | ♦ R/W | 0 | 1097 |  | xN/A | use words 2000, 2001, 2006
397 | P09 Serial Comm | P09.31 | RS485 JOG Command | 0: Stop 1: Jog |  | ♦ R/W | 0 | 1098 |  | xN/A | use words 2000, 2001, 2007
398 | P09 Serial Comm | P09.32 | reserved | n/a |  | n/a | n/a | 1099 |  | xN/A
399 | P09 Serial Comm | P09.33 | GS4 Drive Rated Amps | 0.00~655.34A |  | Read | #.## | 2 | P00 Drive | P00.01 | Rated Current | Display by models |  | Read | ~
400 | P09 Serial Comm | P09.34 | PLC Command Mask (status only) | 0~65535 |  | Read | 0 | 15 | P00 Drive | P00.19 | PLC command mask | bit 0: Control command is forced by PLC control bit 1: Frequency command is forced by PLC control bit 3: Torque command is forced by PLC control |  | Read | 0
401 | P09 Serial Comm | P09.35 | Response Delay Time | 0.0~200.0 ms |  | ♦ R/W | 2 | 442 | P09 Communication | P09.09 | Communication response delay time | 0.0-200.0 ms |  | ♦R/W | 2
402 | P09 Serial Comm | P09.36 | reserved | n/a |  | n/a | n/a | 2000 |  | xN/A
403 | P09 Serial Comm | P09.37 | PLC Address | 1~254 |  | R/W | 2 | 462 | P09 Communication | P09.35 | PLC address | 1-254 |  | R/W | 2
404 | P09 Serial Comm | P09.38 | Firmware Date Code | Format: yywwd • yy = year (2017 = 17) • ww = week (01~52) • d = day of week (1~7; Mon=1, Sun=7) |  | Read | ##### | 2001 |  | xN/A
405 | P09 Serial Comm | P09.39 | Firmware version | x.xx |  | Read | #.## | 8 | P00 Drive | P00.06 | Firmware version | Read only |  | Read | ~
406 | P09 Serial Comm | P09.40 | reserved | n/a |  | n/a | n/a | 2002 |  | xN/A
407 | P09 Serial Comm | P09.41 | GS Series Number | 0~9 |  | Read | 4 | 2003 |  | xN/A | will be P00-18 in future FW
408 | P09 Serial Comm | P09.42 | GS Model ID | 00: GS4-21P0 (230V 1ph/3ph 1.0hp) 01: GS4-22P0 (230V 1ph/3ph 2.0hp) 02: GS4-23P0 (230V 1ph/3ph 3.0hp) 03: GS4-25P0 (230V 3ph 5.0hp) 04: GS4-27P5 (230V 3ph 7.5hp) 05: GS4-2010 (230V 3ph 10hp) 06: GS4-2015 (230V 3ph 15hp) 07: GS4-2020 (230V 3ph 20hp) 08: GS4-2025 (230V 3ph 25hp) 09: GS4-2030 (230V 3ph 30hp) 10: GS4-2040 (230V 3ph 40hp) 11: GS4-2050 (230V 3ph 50hp) 12: GS4-2060 (230V 3ph 60hp) 13: GS4-2075 (230V 3ph 75hp) 14: GS4-2100 (230V 3ph 100hp) 15: GS4-41P0 (460V 3ph 1.0hp) 16: GS4-42P0 (460V 3ph 2.0hp) 17: GS4-43P0 (460V 3ph 3.0hp) 18: GS4-45P0 (460V 3ph 5.0hp) 19: GS4-47P5 (460V 3ph 7.5hp) 20: GS4-4010 (460V 3ph 10hp) 21: GS4-4015 (460V 3ph 15hp) 22: GS4-4020 (460V 3ph 20hp) 23: GS4-4025 (460V 3ph 25hp) 24: GS4-4030 (460V 3ph 30hp) 25: GS4-4040 (460V 3ph 40hp) 26: GS4-4050 (460V 3ph 50hp) 27: GS4-4060 (460V 3ph 60hp) 28: GS4-4075 (460V 3ph 75hp) 29: GS4-4100 (460V 3ph 100hp) 30: GS4-4125 (460V 3ph 125hp) 31: GS4-4150 (460V 3ph 150hp) 32: GS4-4175 (460V 3ph 175hp) 33: GS4-4200 (460V 3ph 200hp) 34: GS4-4250 (460V 3ph 250hp) 35: GS4-4300 (460V 3ph 300hp) |  | Read | ## | 1 | Drive P00 | P00.00 | GS20 Model ID- Identity Code | 102: 120 V, 1 Phase, 0.25 HP 103: 120 V, 1 Phase, 0.5 HP 104: 120 V, 1 Phase, 1 HP 302: 230 V, 1 Phase, 0.25 HP 303: 230 V, 1 Phase, 0.5 HP 304: 230 V, 1 Phase, 1 HP 305: 230 V, 1 Phase, 2 HP 306: 230 V, 1 Phase, 3 HP 202: 230 V, 3 Phase, 0.25 HP 203: 230 V, 3 Phase, 0.5 HP 204: 230 V, 3 Phase, 1 HP 205: 230 V, 3 Phase, 2 HP 206: 230 V, 3 Phase, 3 HP 207: 230 V, 3 Phase, 5 HP 208: 230 V, 3 Phase, 7.5 HP 209: 230 V, 3 Phase, 10 HP 210: 230 V, 3 Phase, 15 HP 211: 230 V, 3 Phase, 20 HP 403: 460 V, 3 Phase, 0.5 HP 404: 460 V, 3 Phase, 1 HP 405: 460 V, 3 Phase, 2 HP 406: 460 V, 3 Phase, 3 HP 407: 460 V, 3 Phase, 5 HP 408: 460 V, 3 Phase, 7.5 HP 409: 460 V, 3 Phase, 10 HP 410: 460 V, 3 Phase, 15 HP 411: 460 V, 3 Phase, 20 HP 412: 460 V, 3 Phase, 25 HP 413: 460 V, 3 Phase, 30 HP 504: 575 V, 3 Phase, 1 HP 505: 575 V, 3 Phase, 2 HP 506: 575 V, 3 Phase, 3 HP 507: 575 V, 3 Phase, 5 HP 508: 575 V, 3 Phase, 7.5 HP 509: 575 V, 3 Phase, 10 HP |  | Read
409 | P09 Serial Comm | P09.43 | Ignore Comm Card Warning | 0: Disable function (do NOT ignore) 1: Enable function (ignore warning) |  | 1 | 1 | 2004 |  | xN/A
410 | P09 Serial Comm | P09.44 | Comm Card Type | 0: No Communication Card 1: reserved 2: reserved 3: reserved 4: MODBUS-TCP Slave 5: EtherNet/IP Slave 6: reserved 7: reserved 8: reserved |  | Read | 0 | 463 | P09 Communication | P09.60 | Communication card identification | 0: No communication card 4: Modbus-TCP slave 5: EtherNet/IP slave 10: Backup power supply |  | Read | 0
411 | P09 Serial Comm | P09.45 | Comm Card Version | 0~65535 |  | Read | 0 | 464 | P09 Communication | P09.61 | Firmware version of communication card | Read only |  | Read | 0
412 | P09 Serial Comm | P09.46 | Comm Card Production Code | 0~65535 |  | Read | 0 | 465 | P09 Communication | P09.62 | Product code | Read only |  | Read | 0
413 | P09 Serial Comm | P09.47 | Comm Card Fault Code | 0~65535 |  | Read | 0 | 466 | P09 Communication | P09.63 | Error code | Read only |  | Read | 0
414 | P09 Serial Comm | P09.48 | Comm Card IP Configuration | 0: Static IP 1: Dynamic IP (DHCP) |  | R/W | 0 | 468 | P09 Communication | P09.75 | Communication card IP configuration (Ethernet) | 0: Static IP 1: Dynamic IP (DHCP) |  | ♦R/W | 0
415 | P09 Serial Comm | P09.49 | Comm Card IP Address Octet 1 | 0~255 |  | R/W | 0 | 469 | P09 Communication | P09.76 | Communication card IP address 1 (Ethernet) | 0-255 |  | ♦R/W | 0
416 | P09 Serial Comm | P09.50 | Comm Card IP Address Octet 2 | 0~255 |  | R/W | 0 | 470 | P09 Communication | P09.77 | Communication card IP address 2 (Ethernet) | 0-255 |  | ♦R/W | 0
417 | P09 Serial Comm | P09.51 | Comm Card IP Address Octet 3 | 0~255 |  | R/W | 0 | 471 | P09 Communication | P09.78 | Communication card IP address 3 (Ethernet) | 0-255 |  | ♦R/W | 0
418 | P09 Serial Comm | P09.52 | Comm Card IP Address Octet 4 | 0~255 |  | R/W | 0 | 472 | P09 Communication | P09.79 | Communication card IP address 4 (Ethernet) | 0-255 |  | ♦R/W | 0
419 | P09 Serial Comm | P09.53 | Comm Card Mask Octet 1 | 0~255 |  | R/W | 0 | 473 | P09 Communication | P09.80 | Communication card address mask 1 (Ethernet) | 0-255 |  | ♦R/W | 0
420 | P09 Serial Comm | P09.54 | Comm Card Mask Octet 2 | 0~255 |  | R/W | 0 | 474 | P09 Communication | P09.81 | Communication card address mask 2 (Ethernet) | 0-255 |  | ♦R/W | 0
421 | P09 Serial Comm | P09.55 | Comm Card Mask Octet 3 | 0~255 |  | R/W | 0 | 475 | P09 Communication | P09.82 | Communication card address mask 3 (Ethernet) | 0-255 |  | ♦R/W | 0
422 | P09 Serial Comm | P09.56 | Comm Card Mask Octet 4 | 0~255 |  | R/W | 0 | 476 | P09 Communication | P09.83 | Communication card address mask 4 (Ethernet) | 0-255 |  | ♦R/W | 0
423 | P09 Serial Comm | P09.57 | Comm Card Gateway Octet 1 | 0~255 |  | R/W | 0 | 477 | P09 Communication | P09.84 | Communication card gateway address 1 (Ethernet) | 0-255 |  | ♦R/W | 0
424 | P09 Serial Comm | P09.58 | Comm Card Gateway Octet 2 | 0~255 |  | R/W | 0 | 478 | P09 Communication | P09.85 | Communication card gateway address 2 (Ethernet) | 0-255 |  | ♦R/W | 0
425 | P09 Serial Comm | P09.59 | Comm Card Gateway Octet 3 | 0~255 |  | R/W | 0 | 479 | P09 Communication | P09.86 | Communication card gateway address 3 (Ethernet) | 0-255 |  | ♦R/W | 0
426 | P09 Serial Comm | P09.60 | Comm Card Gateway Octet 4 | 0~255 |  | R/W | 0 | 480 | P09 Communication | P09.87 | Communication card gateway address 4 (Ethernet) | 0-255 |  | ♦R/W | 0
427 | P09 Serial Comm | P09.61 | reserved | ~ |  | ~ | 0 | 2005 |  | xN/A
428 | P09 Serial Comm | P09.62 | reserved | ~ |  | ~ | 0 | 2006 |  | xN/A
429 | P09 Serial Comm | P09.63 | Comm Card Factory Reset | 0: No Action 1: Reset to the Factory Setting |  | R/W | 0 | 483 | P09 Communication | P09.90 | Reset communication card (Ethernet) | 0: Disable 1: Reset to defaults |  | ♦R/W | 0
430 | P09 Serial Comm | P09.64 | Comm Card External Set | 0, 2 Bit 0 = reserved Bit 1 = Write Ethernet Parameters to Comm Card Bit 2 = reserved |  | R/W | 0 | 2007 |  | xN/A
431 | P09 Serial Comm | P09.65 | reserved | ~ |  | ~ | 0 | 2008 |  | xN/A
432 | P09 Serial Comm | P09.66 | reserved | ~ |  | ~ | ~ | 2009 |  | xN/A
433 | P09 Serial Comm | P09.67 | reserved | ~ |  | ~ | ~ | 2010 |  | xN/A
434 | P09 Serial Comm | P09.68 | reserved | ~ |  | ~ | ~ | 2011 |  | xN/A
435 | P09 Serial Comm | P09.69 | Block Transfer Address Pointer 1 | 0~65535 |  | ♦ R/W | 999 | 2012 |  | xN/A
436 | P09 Serial Comm | P09.70 | Block Transfer Address Pointer 2 |  |  |  |  | 2013 |  | xN/A
437 | P09 Serial Comm | P09.71 | Block Transfer Address Pointer 3 |  |  |  |  | 2014 |  | xN/A
438 | P09 Serial Comm | P09.72 | Block Transfer Address Pointer 4 |  |  |  |  | 2015 |  | xN/A
439 | P09 Serial Comm | P09.73 | Block Transfer Address Pointer 5 |  |  |  |  | 2016 |  | xN/A
440 | P09 Serial Comm | P09.74 | Block Transfer Address Pointer 6 |  |  |  |  | 2017 |  | xN/A
441 | P09 Serial Comm | P09.75 | Block Transfer Address Pointer 7 |  |  |  |  | 2018 |  | xN/A
442 | P09 Serial Comm | P09.76 | Block Transfer Address Pointer 8 |  |  |  |  | 2019 |  | xN/A
443 | P09 Serial Comm | P09.77 | Block Transfer Address Pointer 9 |  |  |  |  | 2020 |  | xN/A
444 | P09 Serial Comm | P09.78 | Block Transfer Address Pointer 10 |  |  |  |  | 2021 |  | xN/A
445 | P09 Serial Comm | P09.79 | Block Transfer Address Pointer 11 |  |  |  |  | 2022 |  | xN/A
446 | P09 Serial Comm | P09.80 | Block Transfer Address Pointer 12 |  |  |  |  | 2023 |  | xN/A
447 | P09 Serial Comm | P09.81 | Block Transfer Address Pointer 13 |  |  |  |  | 2024 |  | xN/A
448 | P09 Serial Comm | P09.82 | Block Transfer Address Pointer 14 |  |  |  |  | 2025 |  | xN/A
449 | P09 Serial Comm | P09.83 | Block Transfer Address Pointer 15 |  |  |  |  | 2026 |  | xN/A
450 | P09 Serial Comm | P09.84 | Block Transfer Address Pointer 16 |  |  |  |  | 2027 |  | xN/A
451 | P09 Serial Comm | P09.85 | PLC Frequency Command Force to 0 | 0~1h Bit 0 = 1: Before PLC scan, set up PLC Target Frequency = 0 |  | R/W | 0 | 461 | P09 Communication | P09.33 | PLC command force to 0 | 0-65535 |  | ♦R/W | 0
452 | P09 Serial Comm | P09.86 | COMM1 Protocol (via RS-485) | 0: Modbus 1: BACnet |  | Read | 0 | 2028 |  | xN/A
453 | P09 Serial Comm | P09.87 | BACnet Address | 0~127 |  | R/W | 10 | 2029 |  | xN/A
454 | P09 Serial Comm | P09.88 | BACnet Baud Rate | 9.6~76.8 Kbps |  | R/W | 38.4 | 2030 |  | xN/A
455 | P09 Serial Comm | P09.89 | BACnet Device Instance Low Word | 0~65535 |  | R/W | 10 | 2031 |  | xN/A
456 | P09 Serial Comm | P09.90 | BACnet Device Instance High Byte | 0~63 |  | R/W | 0 | 2032 |  | xN/A
457 | P09 Serial Comm | P09.91 | BACnet Max Polling Address | 0~127 |  | R/W | 127 | 2033 |  | xN/A
458 | P09 Serial Comm | P09.92 | BACnet Password | 0~65535 |  | R/W | 0 | 2034 |  | xN/A
459 | P09 Serial Comm | P09.93 | Ethernet Comm Card Fault Select | 0: Warn & Continue Operation 1: Warn & Ramp to Stop 2: Warn & Coast to Stop 3: No Warning & Continue Operation |  | ♦ R/W | 3 | 486 | P09 Communication | P09.93 | ENETIP Comm Card Fault Select | 0: Warn & Continue Operation 1: Warn & Ramp to Stop 2: Warn & Coast to Stop 3: No Warning & Continue Operation |  | ♦R/W | 3
460 | P09 Serial Comm | P09.94 | Ethernet Comm Card Time Out Detection | 0: Disable 1: Enable |  | ♦ R/W | 0 | 487 | P09 Communication | P09.94 | ENETIP Comm Card Time Out Detection | 0: Disable 1: Enable |  | ♦R/W | 1
461 | P09 Serial Comm | P09.95 | Ethernet Comm Card Time Out Duration | 0.1 to 100.0 seconds |  | ♦ R/W | 0.5 | 488 | P09 Communication | P09.95 | ENETIP Comm Card Time Out Duration | 0.1 to 100.0 seconds |  | ♦R/W | 3
462 | P09 Serial Comm | P09.96 | reserved | ~ |  | ~ | ~ | 2035 |  | xN/A
463 | P09 Serial Comm | P09.97 | reserved | ~ |  | ~ | ~ | 2036 |  | xN/A
464 | P09 Serial Comm | P09.98 | reserved | ~ |  | ~ | ~ | 2037 |  | xN/A
465 | P09 Serial Comm | P09.99 | reserved | ~ |  | ~ | ~ | 2038 |  | xN/A
466 | P10 Pump | P10.00 | Circulative Control | 0: no function 1: Time Circulation 2: Quantity Cycle 3: Quantity Control 4: Time Circulation + Quantity Cycle 5: Time Circulation + Quantity Control |  | R/W | 0 | 2039 |  | xN/A
467 | P10 Pump | P10.01 | Number of Connected Motors | 1~8 |  | R/W | 1 | 2040 |  | xN/A
468 | P10 Pump | P10.02 | Desired Run Time of Each Motor in Minutes | 0~65500 min |  | R/W | 0 | 2041 |  | xN/A
469 | P10 Pump | P10.03 | Motor Switch Delay Time During Increasing Demand | 0.0~3600.0 sec |  | R/W | 1 | 2042 |  | xN/A
470 | P10 Pump | P10.04 | Motor Switch Delay Time During Decreasing Demand | 0.0~3600.0 sec |  | R/W | 1 | 2043 |  | xN/A
471 | P10 Pump | P10.05 | Aux Motor Switch Delay Time During Fix Amount Circulation in Seconds | 0.0~3600.0 sec |  | ♦ R/W | 10 | 2044 |  | xN/A
472 | P10 Pump | P10.06 | Aux Motor Switch Frequency During Fix Amount Circulation in Hz | 0.00~600.00 Hz |  | ♦ R/W | 60 | 2045 |  | xN/A
473 | P10 Pump | P10.07 | Circulative Control Malfunction Action | 0: Turn Off All Aux 1: Keep Aux Running |  | R/W | 0 | 2046 |  | xN/A
474 | P10 Pump | P10.08 | AUX Motor Stop Frequency | 0.00~600.00 Hz |  | ♦ R/W | 0 | 2047 |  | xN/A
475 | P11 Fault | P11.00 | Fault Output Option 1 | 0: No Error 1~65535: (refer to Fault bit code) |  | ♦R/W | 0 | 301 | P06 Protection | P06.23 | Fault output option 1 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
476 | P11 Fault | P11.01 | Fault Output Option 2 |  |  | ♦R/W | 0 | 302 | P06 Protection | P06.24 | Fault output option 2 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
477 | P11 Fault | P11.02 | Fault Output Option 3 |  |  | ♦R/W | 0 | 303 | P06 Protection | P06.25 | Fault output option 3 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
478 | P11 Fault | P11.03 | Fault Output Option 4 |  |  | ♦R/W | 0 | 304 | P06 Protection | P06.26 | Fault output option 4 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
479 | P11 Fault | P11.04 | First Fault Record | 0: No Error 1: Overcurrent during Accel (ocA) 2: Overcurrent during Decel (ocd) 3: Overcurrent during normal speed (ocn) 4: Ground Fault (GFF) 5: IGBT short circuit (occ) 6: Overcurrent during Stop (ocS) 7: Overvoltage during Accel (ovA) 8: Overvoltage during Decel (ovd) 9: Overvoltage during normal speed (ovn) 10: Overvoltage during Stop (ovS) 11: Low voltage during Accel (LvA) 12: Low voltage during Decel (Lvd) 13: Low voltage during normal speed (Lvn) 14: Low voltage during Stop (LvS) 15: Output ripple / Input phase loss (OrP) 16: IGBT Overheat 1 (oH1) 17: Cap Overheat 2 (oH2) 18: Thermister 1 open (tH1o) 19: Thermister 2 open (tH2o) 20: Power Reset Off (PWR) 21: Overload (oL) (150% 1Min, Inverter) 22: Motor1 Thermal Overload (EoL1) 23: Motor2 Thermal Overload (EoL2) 24: Motor Overheat-PTC (oH3) 25: reserved 26: Over Torque 1 (ot1) 27: Over Torque 2 (ot2) 28: Under current (uc) 29: reserved 30: EEPROM write error (cF1) 31: EEPROM read error (cF2) 32: reserved 33: U phase current sensor detection error (cd1) 34: V phase current sensor detection error (cd2) 35: W phase current sensor detection error (cd3) 36: CC Hardware Logic error 0 (Hd0) 37: OC Hardware Logic error 1 (Hd1) 38: OV Hardware Logic error 2 (Hd2) | 39: OCC Hardware Logic error 3 (Hd3) 40: Motor auto tune error (AuE) 41: PID Feedback loss (AFE) 42~47: reserved 48: Analog input signal loss (ACE) 49: External Fault (EF) 50: Emergency Stop (EF1) 51: Base Block (bb) 52: Password Error (Pcod) 53: Software Code lock (ccod) 54: PC Command error (CE1) 55: PC Address error (CE2) 56: PC Data error (CE3) 57: PC Slave error (CE4) 58: PC Communication Time Out (CE10) 59: PC Keypad Time out (CP10) 60: Braking Transistor Fault (bf) 61: Y-Delta connection Error (ydc) 62: Decel Energy Backup Error (dEb) 63: Over Slip Error (oSL) 64: Electromagnet switch error (ryF) 65~71: reserved 72: STO Loss1 (STL1) STO1~SCM1 internal hardware detect error 73: ES1 Emergency Stop (S1) 74: In Fire Mode (Fire) 75: reserved 76: Safety Torque Off function active (STO) 77: STO Loss2 (STL2) STO2~SCM2 internal hardware detect error 78: STO Loss3 (STL3) – STO1~SCM1 and STO2~SCM2 internal hardware detect errors 79: U Phase Short (Uoc) 80: V Phase Short (Voc) 81: W Phase Short (Woc) 82: U Phase Loss (UPHL) 83: V Phase Loss (VPHL) 84: W Phase Loss (WPHL) 85~89: reserved 90: PLC Force Stop (FStp) 91~96: reserved 97: Ethernet Card Timeout (CD10) 98: reserved 99: CPU Command error (TRAP) 100~110: reserved 111: InrCom Time Out (ictE) | Read | 0 | 294 | P06 Protection | P06.17 | Fault record 1 | 0: No fault record 1: Over-current during acceleration (ocA) 2: Over-current during deceleration (ocd) 3: Over-current during steady operation (ocn) 4: Ground fault (GFF) 6: Over-current at stop (ocS) 7: Over-voltage during acceleration (ovA) 8: Over-voltage during deceleration (ovd) 9: Over-voltage during constant speed (ovn) 10: Over-voltage at stop (ovS) 11: Low-voltage during acceleration (LvA) 12: Low-voltage during deceleration (Lvd) 13: Low-voltage during constant speed (Lvn) 14: Low-voltage at stop (LvS) 15: Phase loss protection (orP) 16: IGBT overheating (oH1) 18: IGBT temperature detection failure (tH1o) 21: Over load (oL) 22: Electronic thermal relay 1 protection (EoL1) 23: Electronic thermal relay 2 protection (EoL2) 24: Motor PTC overheating (oH3) 26: Over torque 1 (ot1) 27: Over torque 2 (ot2) 28: Under current (uC) 31: EEPROM read error (cF2) 33: U-phase error (cd1) 34: V-phase error (cd2) 35: W-phase error (cd3) 36: cc (current clamp) hardware error (Hd0) 37: oc (over-current) hardware error (Hd1) 40: Auto-tuning error (AUE) 41: PID loss AI2 (AFE) 43: PG feedback loss (PGF2) 48: AI2 loss (ACE) 49: External fault (EF) 50: Emergency stop (EF1) 51: External Base Block (bb) 52: Password is locked (Pcod) 54: Illegal command (CE1) 55: Illegal data address (CE2) 56: Illegal data value (CE3) 57: Data is written to read-only address (CE4) 58: Modbus transmission time-out (CE10) | 61: Y-connection / fl-connection switch error (ydc) 62: Deceleration energy backup error (dEb) 63: Over slip error (oSL) 72: STO Loss (STL1) 76: STO (STo) 77: STO Loss 2 (STL2) 78: STO Loss 3 (STL3) 79: U-phase Over-current before run (Aoc) 80: V-phase Over-current before run (boc) 81: W-phase Over-current before run (coc) 82: Output phase loss U phase (oPL1) 83: Output phase loss V phase (oPL2) 84: Output phase loss W phase (oPL3) 87: Low frequency overload protection (oL3) 89: Rotor position detection error (roPd) 111: InrCOM time-out error (ictE) 121: Internal communication error (CP20) 123: Internal communication error (CP22) 124: Internal communication error (CP30) 126: Internal communication error (CP32) 127: Internal communication error (CP33) 128: Over-torque 3 (ot3) 129: Over-torque 4 (ot4) 134: Internal communication error (EoL3) 135: Internal communication error (EoL4) 140: Oc hardware error (Hd6) 141: GFF occurs before run (b4GFF) 142: Auto-tune error 1 (DC test stage) (AuE1) 143: Auto-tune error 2 (High frequency test stage) (AuE2) 144: Auto-tune error 3 (Rotary test stage) (AuE3) | R/W | 0
480 | P11 Fault | P11.05 | Second Most Recent Fault Record |  |  | Read | 0 | 296 | P06 Protection | P06.18 | Fault record 2 | See P06.17 for ranges. |  | R/W | 0
481 | P11 Fault | P11.06 | Third Most Recent Fault Record |  |  | Read | 0 | 297 | P06 Protection | P06.19 | Fault record 3 | See P06.17 for ranges. |  | R/W | 0
482 | P11 Fault | P11.07 | Fourth Most Recent Fault Record |  |  | Read | 0 | 298 | P06 Protection | P06.20 | Fault record 4 | See P06.17 for ranges. |  | R/W | 0
483 | P11 Fault | P11.08 | Fifth Most Recent Fault Record |  |  | Read | 0 | 299 | P06 Protection | P06.21 | Fault record 5 | See P06.17 for ranges. |  | R/W | 0
484 | P11 Fault | P11.09 | Sixth Most Recent Fault Record |  |  | Read | 0 | 300 | P06 Protection | P06.22 | Fault record 6 | See P06.17 for ranges. |  | R/W | 0
486 | P11 Fault | P11.10 | Operating Time of Present Fault Record (Day) | 0~65535 day |  | Read | 0 | 334 | P06 Protection | P06.63 | Operation time of fault record 1 (Days) | 0-65535 days |  | Read | 0
487 | P11 Fault | P11.11 | Operating Time of Present Fault Record (Minute) | 0~1439 min |  | Read | 0 | 335 | P06 Protection | P06.64 | Operation time of fault record 1 (Minutes) | 0-1439 min. |  | Read | 0
488 | P11 Fault | P11.12 | Operating Time of Second Most Recent Fault Record (Day) | 0~65535 day |  | Read | 0 | 336 | P06 Protection | P06.65 | Operation time of fault record 2 (Days) | 0-65535 days |  | Read | 0
489 | P11 Fault | P11.13 | Operating Time of Second Most Recent Fault Record (Minute) | 0~1439 min |  | Read | 0 | 337 | P06 Protection | P06.66 | Operation time of fault record 2 (Minutes) | 0-1439 min. |  | Read | 0
490 | P11 Fault | P11.14 | Operating Time of Third Most Recent Fault Record (Day) | 0~65535 day |  | Read | 0 | 338 | P06 Protection | P06.67 | Operation time of fault record 3 (Days) | 0-65535 days |  | Read | 0
491 | P11 Fault | P11.15 | Operating Time of Third Most Recent Fault Record (Minute) | 0~1439 min |  | Read | 0 | 339 | P06 Protection | P06.68 | Operation time of fault record 3 (Minutes) | 0-1439 min. |  | Read | 0
492 | P11 Fault | P11.16 | Operating Time of Fourth Most Recent Fault Record (Day) | 0~65535 day |  | Read | 0 | 340 | P06 Protection | P06.69 | Operation time of fault record 4 (Days) | 0-65535 days |  | Read | 0
493 | P11 Fault | P11.17 | Operating Time of Fourth Most Recent Fault Record (Minute) | 0~1439 min |  | Read | 0 | 341 | P06 Protection | P06.70 | Operation time of fault record 4 (Minutes) | 0-1439 min. |  | Read | 0
494 | P11 Fault | P11.18 | Frequency Command at Fault | 0.00~655.35 Hz |  | Read | 0 | 309 | P06 Protection | P06.31 | Frequency command at malfunction | 0.00-599.00 Hz |  | Read | 0
495 | P11 Fault | P11.19 | Output Frequency at Fault | 0.00~655.35 Hz |  | Read | 0 | 310 | P06 Protection | P06.32 | Output frequency at malfunction | 0.00-599.00 Hz |  | Read | 0
496 | P11 Fault | P11.20 | Output Voltage at Fault | 0.0~6553.5V |  | Read | 0 | 311 | P06 Protection | P06.33 | Output voltage at malfunction | 0.0-6553.5 V |  | Read | 0
497 | P11 Fault | P11.21 | DC Bus Voltage at Fault | 0.0~6553.5V |  | Read | 0 | 312 | P06 Protection | P06.34 | DC bus voltage at malfunction | 0.0-6553.5 V |  | Read | 0
498 | P11 Fault | P11.22 | Output Current at Fault | 0.00~655.35A |  | Read | 0 | 313 | P06 Protection | P06.35 | Output current at malfunction | 0.00-655.35 Amp |  | Read | 0
499 | P11 Fault | P11.23 | IGBT Temperature at Fault | -3276.7 to 3276.7 °C |  | Read | 0 | 314 | P06 Protection | P06.36 | IGBT temperature at malfunction | -3276.7-3276.70C |  | Read | 0
500 | P11 Fault | P11.24 | HeatSink Temperature at Fault | -3276.7 to 3276.7 °C |  | Read | 0 | 2050 |  | xN/A
501 | P11 Fault | P11.25 | RPM of Motor at Fault | -32767 to 32767 rpm |  | Read | 0 | 315 | P06 Protection | P06.38 | Motor speed at malfunction | -32767-32767 rpm |  | Read | 0
502 | P11 Fault | P11.26 | Digital Input Status at Fault | 0~65535 |  | Read | 0 | 317 | P06 Protection | P06.40 | Status of the digital input terminal at malfunction | 0000h-FFFFh |  | Read | 0
503 | P11 Fault | P11.27 | Digital Output Status at Fault | 0~65535 |  | Read | 0 | 318 | P06 Protection | P06.41 | Status of the digital output terminal at malfunction | 0000h-FFFFh |  | Read | 0
504 | P11 Fault | P11.28 | Drive Status at Fault | 0~65535 |  | Read | 0 | 319 | P06 Protection | P06.42 | Drive status at malfunction | 0000h-FFFFh |  | Read | 0

## Crossref_GS2 full
GS2 Parameter Summary | [5 empty] | GS20 Parameter Summary
GS2 Seq | GS2 Parameter Group | GS2 Parameter | Description | Range | Default | GS20Seq | Parameter Group | Parameter No. | Parameter Description | Range | Range (con't) | R/W | Default | Key Difference to Note from GS2 | SEE DISCLAIMER
1 | P00 Motor | P0.00 | Motor Nameplate Voltage | 115V/230V: 200/208/220/230/240 460V: 380/400/415/440/460/480 575V: 380 to 637 | 240 480 575 | 34 | P01 Basic | P01.02 | Motor 1, Rated Voltage (Nameplate) | 120V / 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V 575V models: 0.0-637.0 V |  | R/W | 220.0 440.0 575.0
2 | P00 Motor | P0.01 | Motor Nameplate Amps | Drive Rated Amps X .3 to 1.0 | Drive Rated Amps x 1.0 | 222 | P05 Motor | P05.01 | Induction Motor 1, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
3 | P00 Motor | P0.02 | Motor Base Frequency | 50/60/400 | 60 | 33 | P01 Basic | P01.01 | Motor 1 Fbase | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00 | 0.00–599.00 Hz
4 | P00 Motor | P0.03 | Motor Base RPM | 375 to 9999 RPM | 1750 | 224 | P05 Motor | P05.03 | Induction Motor 1, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
5 | P00 Motor | P0.04 | Motor Maximum RPM | P0.03 to 9999 RPM | P0.03 | 32 | P01 Basic | P01.00 | Maximum operation frequency | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00 | GS20 set max hertz as drive limit, not RPM.
6 | P01 Ramps | P1.00 | Stop Methods | 00: Ramp to Stop 01: Coast to Stop | 0 | 17 | P00 Drive | P00.22 | Stop method | 0: Ramp to stop 1: Coast to stop |  | ♦R/W | 0
7 | P01 Ramps | P1.01 | Acceleration Time 1 | 0.1 to 600.0 sec | 10 | 44 | P01 Basic | P01.12 | Acceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
8 | P01 Ramps | P1.02 | Deceleration Time 1 | 0.1 to 600.0 sec | 30 | 45 | P01 Basic | P01.13 | Deceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
9 | P01 Ramps | P1.03 | Accel S-curve | 0 to 7 | 0 | 56 | P01 Basic | P01.24 | S-curve for acceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
10 | P01 Ramps | P1.03 |  |  |  | 57 | P01 Basic | P01.25 | S-curve for acceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
11 | P01 Ramps | P1.04 | Decel S-curve | 0 to 7 | 0 | 58 | P01 Basic | P01.26 | S-curve for deceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
12 | P01 Ramps | P1.04 |  |  |  | 59 | P01 Basic | P01.27 | S-curve for deceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
13 | P01 Ramps | P1.05 | Acceleration Time 2 | 0.1 to 600.0 sec | 10 | 46 | P01 Basic | P01.14 | Acceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
14 | P01 Ramps | P1.06 | Deceleration Time 2 | 0.1 to 600.0 sec | 30 | 47 | P01 Basic | P01.15 | Deceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
15 | P01 Ramps | P1.07 | Select method to use 2nd Accel/Decel | 00: RMP2 from DI terminal 01: Transition Frequencies P1.08 & P1.09 | 0 | 104 | P02 Digital IO | P02.06* P02.03 - P02.07 | Multifunction Inputs Command for P02.03 - P02.07 |  |  |  |  | Choose any Dix input with Function 8-1st and 2nd acceleration / deceleration time selection
16 | P01 Ramps | P1.08 | Accel 1 to Accel 2 frequency transition | 0.0 to 400.0 Hz | 0 | 55 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | 0.00-599.00 Hz |  | ♦R/W | 0 | Set 3 parameters..P01.18,19 and 23. Switch Frequency between First and Fourth Accel./Decel. Must use 4th accel settings, not 2nd.
17 | P01 Ramps | P1.08 |  |  |  | 50 | P01 Basic | P01.18 | Acceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0 | *external terminal has priority over this parameter
18 | P01 Ramps | P1.08 |  |  |  | 51 | P01 Basic | P01.19 | Deceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
19 | P01 Ramps | P1.09 | Decel 2 to Decel 1 frequency transition | 0.0 to 400.0 Hz | 0 |  |  | xN/A | [5 empty] | * accel and decel must be at same frequency and configured between 1st and 4th accel/decel only. No equivalent P01.09 parameter
20 | P01 Ramps | P1.10 | Skip Frequency 1 | 0.0 to 400.0 Hz | 0 | 60 | P01 Basic | P01.28 | Skip frequency 1 (upper limit) | 0.00-599.00 Hz |  | R/W | 0 | 0.00–599.00 Hz- Use Upper and lower setting
21 | P01 Ramps | P1.10 |  |  |  | 61 | P01 Basic | P01.29 | Skip frequency 1 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
22 | P01 Ramps | P1.11 | Skip Frequency 2 | 0.0 to 400.0 Hz | 0 | 62 | P01 Basic | P01.30 | Skip frequency 2 (upper limit) | 0.00-599.00 Hz |  | R/W | 0 | 0.00–599.00 Hz- Use Upper and lower setting
23 | P01 Ramps | P1.11 |  |  |  | 63 | P01 Basic | P01.31 | Skip frequency 2 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
24 | P01 Ramps | P1.12 | Skip Frequency 3 | 0.0 to 400.0 Hz | 0 | 64 | P01 Basic | P01.32 | Skip frequency 3 (upper limit) | 0.00-599.00 Hz |  | R/W | 0 | 0.00–599.00 Hz- Use Upper and lower setting
25 | P01 Ramps | P1.12 |  |  |  | 65 | P01 Basic | P01.33 | Skip frequency 3 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
26 | P01 Ramps | P1.17 | Skip Frequency Band | 0.0 to 20.0 Hz | 0 | 710 |  | xN/A | [5 empty] | Band not Utilized since Skip Freq has upper and lower settting
27 | P01 Ramps | P1.18 | DC Injection Current Level | 00 to 100 % | 0 | 346 | P07 Special | P07.01 | DC brake current level | 0-100% |  | ♦R/W | 0
28 | P01 Ramps | P1.20 | DC Injection during Start-up | 0.0 to 5.0 sec | 0 | 347 | P07 Special | P07.02 | DC brake time at start-up | 0.0-60.0 sec. |  | ♦R/W | 0 | 0.0–60.0 sec.
29 | P01 Ramps | P1.21 | DC Injection during Stopping | 0.0 to 25.0 sec | 0 | 348 | P07 Special | P07.03 | DC brake time at STOP | 0.0-60.0 sec. |  | ♦R/W | 0 | 0.0–60.0 sec.
30 | P01 Ramps | P1.22 | Start-point for DC Injection | 0.0 to 60.0 Hz | 0 | 349 | P07 Special | P07.04 | DC brake frequency at STOP | 0.00-599.00 Hz |  | ♦R/W | 0
31 | P02 V/Hz | P2.00 | Volts/Hertz Settings |  | 0 | 11 | P00 Drive | P00.11 | Speed (Velocity) Control mode | 0: IMVF (V/F control) 1: IMVFPG (V/F control + encoder) 2: IM/PM SVC (IM or PM space vector control) 5: IMFOC Sensorless (field-oriented sensorless vector control) Note: For option 2 (SVC), see P05.33 for induction motor (IM) or permanent magnent (PM) motor selection. |  | R/W | 0 | For Control mode: First, Ensure V/F Mode is selected
31 | P02 V/Hz | P2.00 | Volts/Hertz Settings | 00: General Purpose 01: High Starting Torque 02: Fans and Pumps 03: Custom | 0 | 75 | P01 Basic | P01.43 | V/F curve selection | 0: V/F curve determined by P01.00-P01.08 1: V/F curve to the power of 1.5 2: V/F curve to the power of 2 |  | R/W | 0 | Second, Select the curve, or
31 | P02 V/Hz | P2.00 | Volts/Hertz Settings |  | 0 | 555 | P13 Macro/User | P13.00 | Industry-specific parameter application | 00: Disabled 01: User-defined parameter 02: Compressor 03: Fan 04: Pump 05: Conveyor 06: Machine tool 07: Packing 08: Textiles 10: Logistics 11: Tension PID 12: Tension PID + master / auxiliary frequency |  | R/W | 0 | Third, choose the Industry specific application setting
32 | P02 V/Hz | P2.01 | Slip Compensation | 0.0 to 10.0 | 0 | 372 | P07 Special | P07.27 | Slip compensation gain (V/F and SVC control mode) | 0.00-10.00 |  | ♦R/W | 0.00 (Default value is 1.00 in SVC mode)
33 | P02 V/Hz | P2.02 | Auto-torque Boost | 00 to 10 | 0 | 371 | P07 Special | P07.26 | Torque compensation gain (V/F and SVC control mode) | IM: 0-10 (when P05.33 = 0) PM: 0-5000 (when P05.33 = 1 or 2) |  | ♦R/W | 1
34 | P02 V/Hz | P2.04 | Mid-point Frequency | 0.1 to 400 Hz | 1.5 | 35 | P01 Basic | P01.03 | Motor 1, Mid-point frequency 1 | 0.00-599.00 Hz |  | R/W | 3
35 | P02 V/Hz | P2.05 | Mid-point Voltage | 115V/230V: 2.0 to 255V 460V: 2.0 to 510V 575V: 2.0 to 637V | 10.0 20.0 24.0 | 36 | P01 Basic | P01.04 | Motor 1, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 11.0 22.0 40.0
36 | P02 V/Hz | P2.06 | Min. Output Frequency | 0.1 to 20.0 Hz | 1.5 | 39 | P01 Basic | P01.07 | Motor 1, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
37 | P02 V/Hz | P2.07 | Min. Output Voltage | 115V/230V: 2.0 to 50.0V 460V: 2.0 to 100.0V 575V: 2.0 to 130.6V | 10.0 20.0 24.0 | 40 | P01 Basic | P01.08 | Motor 1, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 1.0 2.0 16.7
38 | P02 V/Hz | P2.08 | PWM Carrier Frequency | 115V/230V/460V; 01 to 15 kHz 575V; 01 to 10 kHz | 12 6 | 13 | P00 Drive | P00.17 | Carrier frequency | Variable Torque: 2-15 kHz Constant Torque: 2-15 kHz Note: When P00-11=5 (IMFOC Sensorless), the maximum setting value for the carrier frequency is 10 kHz. |  | R/W | 4 | 2-15 kHz
39 | P03 Digital | P3.00 | Source of Operation Command | 00: Operation determined by digital keypad 01: Operation determined by external control terminals, keypad STOP is enabled 02: Operation determined by external control terminals, keypad STOP is disabled 03: Operation determined by RS-485 interface, keypad STOP is enabled 04: Operation determined by RS-485 interface, keypad STOP is disabled | 0 | 16 | P00 Drive | P00.21 P00.31 | Operation command source (AUTO, REMOTE) | 0: Digital keypad 1: External terminals 2: RS-485 communication input 3: Not used 5: Communication card Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function settings 41/42 or 56 or with GS4-KPD (optional) |  | R/W | 0 | 0-6
40 | P03 Digital | P3.00 |  |  |  | 26 | P00 Drive | P00.32 | Digital keypad STOP function | 0: STOP key disabled 1: STOP key enabled |  | ♦R/W | 0 | 0: STOP key disabled 1: STOP key enabled
41 | P03 Digital | P3.01 | Multi-function Input Terminals (DI1 - DI2) | 00: DI1 - FWD / STOP, DI2 - REV / STOP 01: DI1 - RUN / STOP, DI2- REV / FWD 02: DI1 - RUN momentary (N.O.) DI2 - REV / FWD DI3 - STOP momentary (N.C.) | 0 | 99 | P02 Digital IO | P02.00 | Two-wire / threewire operation control | 0: No function 1: Two-wire mode 1, power on for operation control (DI1: FWD/STOP, DI2: REV/STOP) 2: Two-wire mode 2, power on for operation control (DI1: RUN/STOP, DI2: REV/FWD) 3: Three-wire, power on for operation control (DI1: RUN, DI2: REV/FWD, DI3: STOP) 4: Two-wire mode 1, Quick Start (DI1: FWD/STOP, DI2: REV/STOP) 5: Two-wire mode 2, Quick Start (DI1: RUN/STOP, DI2: REV/FWD) 6: Three-wire, Quick Start (DI1: RUN, DI2: REV/FWD, DI3: STOP) | 50: Slave dEb action to execute 51: Selection for PLC mode bit 0 52: Selection for PLC mode bit 1 56: Local / Remote selection 58: Enable fire mode (with RUN command) 59: Enable fire mode (without RUN command) 70: Force auxiliary frequency return to 0 71: Disable PID function, force PID output return to 0 72: Disable PID function, retain the output value before disabled 73: Force PID integral gain return to 0, disable integral 74: Reverse PID feedback 81: Simple positioning zero point position signal input 82: OOB loading balance detection 83: Multi-motor (IM) selection bit 0 84: Multi-motor (IM) selection bit 1 | R/W | 0
42 | P03 Digital | P3.01 |  |  |  | 99.1 | P02 Digital IO | P02.01 | Multi-function input command 1 (FWD/DI1) | 0: No function 1: Multi-step speed command 1 / multi-step position command 1 2: Multi-step speed command 2 / multi-step position command 2 3: Multi-step speed command 3 / multi-step position command 3 4: Multi-step speed command 4 / multi-step position command 4 5: Reset 6: JOG [by external control or GS4- KPD (optional)] 7: Acceleration / deceleration speed inhibit 8: 1st and 2nd acceleration / deceleration time selection 9: 3rd and 4th acceleration / deceleration time selection 10: External Fault (EF) Input (P07.20) 11: Base Block (B.B.) input from external source 12: Output stop 13: Cancel the setting of auto- acceleration / auto-deceleration time 15: Rotating speed command from AI1 16: Rotating speed command from AI2 18: Force to stop (P07.20) 19: Digital up command 20: Digital down command 21: PID function disabled 22: Clear the counter 23: Input the counter value (DI6) 24: FWD JOG command 25: REV JOG command 26: TQC / Field Oriented Control (FOC) mode selection 27: ASR1 / ASR2 selection 28: Emergency stop (EF1) 29: Signal confirmation for Y-connection 30: Signal confirmation for ti. -connection 31: High torque bias (P11.30) 32: Middle torque bias (P11.31) 33: Low torque bias (P11.32) 38: Disable writing EEPROM function 39: Torque command direction 40: Force coasting to stop 41: HAND switch 42: AUTO switch 48: Mechanical gear ratio switch 49: Enable drive | 50: Slave dEb action to execute 51: Selection for PLC mode bit 0 52: Selection for PLC mode bit 1 56: Local / Remote selection 58: Enable fire mode (with RUN command) 59: Enable fire mode (without RUN command) 70: Force auxiliary frequency return to 0 71: Disable PID function, force PID output return to 0 72: Disable PID function, retain the output value before disabled 73: Force PID integral gain return to 0, disable integral 74: Reverse PID feedback 81: Simple positioning zero point position signal input 82: OOB loading balance detection 83: Multi-motor (IM) selection bit 0 84: Multi-motor (IM) selection bit 1 | R/W | 0 | 0-84 only use if P02.00 = 0
43 | P03 Digital | P3.01 |  |  |  | 100 | P02 Digital IO | P02.02 | Multi-function input command 2 (REV/DI2) | See P02.01 for values. |  | R/W | 0 | 0-84only use if P02.00 = 0
44 | P03 Digital | P3.02 | Multi-function Input (DI3) | 00: External Fault (N.O.) 01: External Fault (N.C.) 02: External Reset 03: Multi-Speed/PID SP Bit 1 04: Multi-Speed/PID SP Bit 2 05: Multi-Speed/PID SP Bit 3 06: Reserved 07: Reserved 08: Reserved 09: Jog 10: External Base Block (N.O.) 11: External Base Block (N.C.) 12: Second Accel/Decel Time 13: Speed Hold 14: Increase Speed 15: Decrease Speed 16: Reset Speed to Zero 17: PID Disable (N.O.) 18: PID Disable (N.C.) 99: Input Disable | 0 | 101 | P02 Digital IO | P02.03 | Multi-function input command 3 (DI3) | See P02.01 for values. |  | R/W | 1 | 0-84
45 | P03 Digital | P3.03 | Multi-function Input (DI4) |  | 3 | 102 | P02 Digital IO | P02.04 | Multi-function input command 4 (DI4) | See P02.01 for values. |  | R/W | 2 | 0-84
46 | P03 Digital | P3.04 | Multi-function Input (DI5) |  | 4 | 103 | P02 Digital IO | P02.05 | Multi-function input command 5 (DI5) | See P02.01 for values. |  | R/W | 3 | 0-84
47 | P03 Digital | P3.05 | Multi-function Input (DI6) |  | 5 | 104 | P02 Digital IO | P02.06 | Multi-function input command 6 (DI6) | See P02.01 for values. |  | R/W | 4 | 0-84
48 | P03 Digital | P3.11 | Multi-Function Output Terminal 1 | 00: AC Drive Running 01: AC Drive Fault 02: At Speed 03: Zero Speed 04: Above Desired Frequency 05: Below Desired Frequency 06: At Maximum Speed 07: Over torque detected 08: Above Desired Current 09: Below Desired Current 10: PID Deviation Alarm | 0 | 110 | P02 Digital IO | P02.13 | Multi-function output 1 (R1) | 0: No function 1: Indication during RUN 2: Operation speed reached 3: Desired frequency reached 1 (P02.22) 4: Desired frequency reached 2 (P02.24) 5: Zero speed (Frequency command) 6: Zero speed including STOP (Frequency command) 7: Over-torque 1 (P06.06-06.08) 8: Over-torque 2 (P06.09-06.11) 9: Drive is ready 10: Low voltage warning (Lv) (P06.00) 11: Malfunction indication 13: Overheat warning (P06.15) 14: Software brake signal indicator (P07.00) 15: PID feedback error (P08.13, P08.14) 16: Slip error (oSL) 17: Count value reached, does not return to 0 (P02.20) 18: Count value reached, return to 0 (P02.19) 19: External interrupt B.B. input (Base Block) 20: Warning output 21: Over-voltage 22: Over-current stall prevention 23: Over-voltage stall prevention 24: Operation mode 25: Forward command 26: Reverse command 29: Output when frequency � P02.34 30: Output when frequency < P02.34 31: Y-connection for the motor coil 32: t.-connection for the motor coil 33: Zero speed (actual output frequency) 34: Zero speed including STOP (actual output frequency) 35: Error output selection 1 (P06.23) 36: Error output selection 2 (P06.24) 37: Error output selection 3 (P06.25) 38: Error output selection 4 (P06.26) 40: Speed reached (including STOP) 42: Crane function 43: Motor speed detection 44: Low current output (use with P06.71-06.73) 45: UVW output electromagnetic valve switch 46: Master dEb output | 51: Analog output control for RS-485 interface 52: Output control for communication cards 53: Fire mode indication 66: SO output logic A 67: Analog input level reached 68: SO output logic B 73: Over-torque 3 74: Over-torque 4 75: Forward RUN status 76: Reverse RUN status | ♦R/W | 11 | 0-75
49 | P03 Digital | P3.12 | Multi-Function Output Terminal 2 | same as P3.11 | 1 | 112 | P02 Digital IO | P02.16 | Multi-function output 2 (DO1) | See P02.16 for values. |  | ♦R/W | 0 | 0-75; Multi-function output 3 (DO2)- Transisitor output, not relay output..ensure adequante current for field device
50 | P03 Digital | P3.16 | Desired Frequency | 0.0 to 400.0 Hz | 0 | 117 | P02 Digital IO | P02.22 | Desired frequency reached 1 | 0.00-599.00 Hz |  | ♦R/W | 60.00 / 50.00
51 | P03 Digital | P3.17 | Desired Current | 0.0 to <Drive Rated Amps> | 0 |  |  | xN/A
52 | P03 Digital | P3.18 | PID Deviation Level | 1.0 to 50.0 % | 10 | 402 | P08 Hi Func PID | P08.13 | PID feedback signal error deviation level | 1.0-50.0% |  | ♦R/W | 10
53 | P03 Digital | P3.19 | PID Deviation Time | 0.1 to 300.0 sec | 5 | 403 | P08 Hi Func PID | P08.14 | PID feedback signal error deviation detection time | 0.1-300.0 sec. |  | ♦R/W | 5
54 | P04 Analog | P4.00 | Source of Frequency Command | 00: Frequency determined by keypad potentiometer 01: Frequency determined by digital keypad up/down 02: Frequency determined by 0 to +10V input on AI terminal with jumpers 03: Frequency determined by 4 to 20mA input on AI terminal with jumpers 04: Frequency determined by 0 to 20mA input on AI terminal with jumpers 05: Frequency determined by RS-232C/ RS-485 communication interface | 0 | 15 | P00 Drive | P00.20 | Master frequency command source (AUTO, REMOTE) | 0: Digital keypad 1: RS-485 communication input 2: External analog input (Refer to P03.00) 3: External UP / DOWN terminal (digital input terminals) 4: Pulse input (DI7) without direction command (refer to P10.16 for pulse input config) 6: Not used 7: Digital keypad VR/potentiometer dial (GS20 only) 8: Communication card 9: PID controller Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0 | 0-9
55 | P04 Analog | P4.00 |  |  |  | 137 | P03 Analog IO | P03.01 | Analog input selection (AI2) |  |  | ♦R/W | 0 | 0-13
56 | P04 Analog | P4.01 | Analog Input Offset Polarity | 00: No Offset 01: Positive Offset 02: Negative Offset | 0 | 141 | P03 Analog IO | P03.08 | Positive / negative bias mode (AI2) | 0: No bias 1: Lower than or equal to bias 2: Greater than or equal to bias 3: The absolute value of the bias voltage while serving as the center 4: Bias serves as the center |  | ♦R/W | 0 | 4 different mode in GS20
57 | P04 Analog | P4.02 | Analog Input Offset | 0.0 to 100.0% | 0 | 139 | P03 Analog IO | P03.04 | Analog input bias (AI2) | -100.0-100.0% |  | ♦R/W | 0 | -100 - 100%, calcs work differently in GS20
58 | P04 Analog | P4.03 | Analog Input Gain | 0.0 to 300.0% | 100 | 144 | P03 Analog IO | P03.12 | Analog input gain (AI2) | -500.0-500.0% |  | ♦R/W | 100 | -500 - 500%, calcs work differentin in GS20
59 | P04 Analog | P4.04 | Analog Input Reverse Motion Enable | 00: Forward Motion Only 01: Reverse Motion Enable | 0 | 142 | P03 Analog IO | P03.10 | Reverse setting when analog signal input is negative frequency | 0: Negative frequency input is not allowed. The digital keypad or external terminal controls the forward and reverse direction. 1: Negative frequency input is allowed. Positive frequency = run in a forward direction; negative frequency = run in a reverse direction. The digital keypad or external terminal control cannot change the running direction. |  | ♦R/W | 0
60 | P04 Analog | P4.05 | Loss of ACI Signal (4-20mA) | 00: Decelerate to 0Hz 01: Stop immediately and display error code “EF” 02: Continue operation by the last frequency command | 0 | 148 | P03 Analog IO | P03.19 | Signal loss selection for analog input 4-20 mA | 0: Disable 1: Continue operation at the last frequency 2: Decelerate to 0 Hz 3: Stop immediately and display "ACE" |  | ♦R/W | 0 | 0-3
61 | P04 Analog | P4.11 | Analog Output Signal | 00: frequency Hz 01: Current A 02: PV | 0 | 149 | P03 Analog IO | P03.20 | Multi-function output (A01) | 0: Output frequency (Hz) 1: Frequency command (Hz) 2: Motor speed (Hz) 3: Output current (rms) 4: Output voltage 5: DC bus voltage 6: Power factor 7: Power 8: Output torque 9: AI1 10: AI2 12: Iq current command 13: Iq feedback value 14: Id current command 15: Id feedback value 16: Vq-axis voltage command 17: Vd-axis voltage command 18: Torque command 19: PG2 (DI7) frequency command 21: RS-485 analog output 22: Communication card analog output 23: Constant voltage output |  | ♦R/W | 0
62 | P04 Analog | P4.12 | Analog Output Gain | 00 to 200% | 100 | 150 | P03 Analog IO | P03.21 | Analog output gain (A01) | 0.0-500.0% |  | ♦R/W | 100 | 0-500%
63 | P05 Presets | P5.00 | Jog | 0.0 to 400.0 Hz | 6 | 54 | P01 Basic | P01.22 | JOG frequency | 0.00-599.00 Hz |  | ♦R/W | 6 | 0.00–599.00 Hz
64 | P05 Presets | P5.01 | Multi-Speed 1 | 0.0 to 400.0 Hz | 0 | 186 | P04 Multi Step Spd | P04.00 | 1st step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
65 | P05 Presets | P5.02 | Multi-Speed 2 | 0.0 to 400.0 Hz | 0 | 187 | P04 Multi Step Spd | P04.01 | 2nd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
66 | P05 Presets | P5.03 | Multi-Speed 3 | 0.0 to 400.0 Hz | 0 | 188 | P04 Multi Step Spd | P04.02 | 3rd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
67 | P05 Presets | P5.04 | Multi-Speed 4 | 0.0 to 400.0 Hz | 0 | 189 | P04 Multi Step Spd | P04.03 | 4th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
68 | P05 Presets | P5.05 | Multi-Speed 5 | 0.0 to 400.0 Hz | 0 | 190 | P04 Multi Step Spd | P04.04 | 5th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
69 | P05 Presets | P5.06 | Multi-Speed 6 | 0.0 to 400.0 Hz | 0 | 191 | P04 Multi Step Spd | P04.05 | 6th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
70 | P05 Presets | P5.07 | Multi-Speed 7 | 0.0 to 400.0 Hz | 0 | 192 | P04 Multi Step Spd | P04.06 | 7th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
71 | P06 Protection | P6.00 | Electronic Thermal Overload Relay | 00: Constant Torque 01: Variable Torque 02: Inactive | 0 | 285 | P06 Protection | P06.13 | Electronic thermal relay selection 1 (motor 1) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with fan on the shaft) 2: Disabled |  | ♦R/W | 2
72 | P06 Protection | P6.01 | Auto Restart after Fault | 00 to 10 | 0 | 357 | P07 Special | P07.11 | Number of times of restart after fault | 0-10 |  | ♦R/W | 0
73 | P06 Protection | P6.02 | Momentary Power Loss | 00: Stop operation after momentary power loss 01: Continue operation after momentary power loss, speed search from Speed Reference 02: Continue operation after momentary power loss, speed search from Minimum Speed | 0 | 352 | P07 Special | P07.06 | Restart after momentary power loss | 0: Stop operation 1: Speed tracking by the speed before the power loss 2: Speed tracking by the minimum output frequency |  | ♦R/W | 0
74 | P06 Protection | P6.03 | Reverse Operation Inhibit | 00: Enable Reverse Operation 01: Disable Reverse Operation | 0 | 18 | P00 Drive | P00.23 | Motor direction control | 0: Enable forward / reverse 1: Disable reverse 2: Disable forward |  | ♦R/W | 0 | 0: Enable forward / reverse 1: Disable reverse 2: Disable forward
75 | P06 Protection | P6.04 | Auto Voltage Regulation | 00: AVR enabled 01: AVR disabled 02: AVR disabled during decel 03: AVR disabled during stop | 0 | 368 | P07 Special | P07.23 | Automatic voltage regulation (AVR) function | 0: Enable AVR 1: Disable AVR 2: Disable AVR during deceleration |  | ♦R/W | 0
76 | P06 Protection | P6.05 | Over-Voltage Stall Prevention | 00: Enable Over-voltage Stall Prevention 01: Disable Over-voltage Stall Prevention | 0 | 273 | P06 Protection | P06.01 | Over-voltage stall prevention | 0: Disable 120V / 230V models: 0.0-390.0 VDC 460V models: 0.0-900.0 VDC 575V models: 0.0-1000.0 VDC |  | ♦R/W | 380.0 760.0 975.0
77 | P06 Protection | P6.06 | Auto Adjustable Accel/Decel | 00: Linear Accel/Decel 01: Auto Accel, Linear Decel 02: Linear Accel, Auto Decel 03: Auto Accel/Decel 04: Auto Accel/Decel Stall Prevention (limited by P1.01, P1.02, P1.05, P1.06) | 0 | 76 | P01 Basic | P01.44 | Auto-acceleration and auto-deceleration setting | 0: Linear acceleration and deceleration 1: Auto-acceleration and linear deceleration 2: Linear acceleration and auto- deceleration 3: Auto-acceleration and auto- deceleration 4: Stall prevention by auto- acceleration and auto-deceleration (limited by P01.12 -P01.21) |  | ♦R/W | 0
78 | P06 Protection | P6.07 | Over-Torque Detection Mode | 00: Disabled 01: Enabled during constant speed operation 02: Enabled during acceleration | 0 | 278 | P06 Protection | P06.06 | Over-torque detection selection (motor 1) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN |  | ♦R/W | 0 | 0-4
79 | P06 Protection | P6.08 | Over-Torque Detection Level | 30 to 200% | 150 | 279 | P06 Protection | P06.07 | Over-torque detection level (motor 1) | 10-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 120 | 10-250% (100% corresponds to the rated current of the drive)
80 | P06 Protection | P6.09 | Over-Torque Detection Time | 0.1 to 10.0 | 0.1 | 280 | P06 Protection | P06.08 | Over-torque detection time (motor 1) | 0.1-60.0 sec. |  | ♦R/W | 0.1 | 0.1-60.0 sec.
81 | P06 Protection | P6.10 | Over-Current Stall Prevention during Acceleration | 20 to 200% | 150 | 275 | P06 Protection | P06.03 | Over-current stall prevention during acceleration (OCA) | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive) |  | ♦R/W | 180 | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive)
82 | P06 Protection | P6.11 | Over-Current Stall Prevention during Operation | 20 to 200% | 150 | 276 | P06 Protection | P06.04 | Over-current stall prevention during operation (OCN) | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive) |  | ♦R/W | 180 | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive)
83 | P06 Protection | P6.12 | Maximum Allowable Power Loss Time | 0.3 to 5.0 sec | 2 | 353 | P07 Special | P07.07 | Allowed power loss duration | 0.0-20.0 sec. |  | ♦R/W | 2 | 0.0-20.0 sec.
84 | P06 Protection | P6.13 | Base-Block Time for Speed Search | 0.3 to 5.0 sec | 0.5 | 354 | P07 Special | P07.08 | Base Block time | 0.0-60.0 sec. |  | ♦R/W | 0.5 | 0.0-60.0 sec.
85 | P06 Protection | P6.14 | Maximum Speed Search Current Level | 30 to 200% | 150 | 355 | P07 Special | P07.09 | Current limit of speed tracking | 20-200% |  | ♦R/W | 100 | 20-200%
86 | P06 Protection | P6.15 | Upper Bound of Output Frequency | 0.1 to 400Hz | 400 | 42 | P01 Basic | P01.10 | Output frequency upper limit | 0.00-599.00 Hz |  | ♦R/W | 599
87 | P06 Protection | P6.16 | Lower Bound of Output Frequency | 0.0 to 400Hz | 0 | 43 | P01 Basic | P01.11 | Output frequency lower limit | 0.00-599.00 Hz |  | ♦R/W | 0
88 | P06 Protection | P6.30 | Line Start Lockout | 00: Enable Line Start Lockout 01: Disable Line Start Lockout | 0 | 122 | P02 Digital IO | P02.35 | External operation control selection after fault reset and reboot | 0: Disable 1: Drive runs if the RUN command remains after reset or reboot |  | ♦R/W | 0 | 0: Disable 1: Drive runs if the RUN command remains after reset or reboot
89 | P06 Protection | P6.31 | Present Fault Record | 00: No Fault occurred 01: Over-current (oc) 02: Over-voltage (ov) 03: Overheat (oH) 04: Overload (oL) 05: Overload 1 (oL1) 06: Overload 2 (oL2) 07: External Fault (EF) 08: CPU failure 1 (CF1) 09: CPU failure 2 (CF2) 10: CPU failure 3 (CF3) 11: Hardware Protection Failure (HPF) 12: Over-current during accel (OCA) 13: Over-current during decel (OCd) 14: Over-current during steady state (OCn) 15:Ground fault or fuse failure (GFF) 16: Reserved 17: Input power 3-phase loss 18: External Base-Block (bb) 19: Auto Adjust accel/decel failure (cFA) 20: Software protection code (codE) | 0 | 289 | P06 Protection | P06.17 | Fault record 1 | 0: No fault record 1: Over-current during acceleration (ocA) 2: Over-current during deceleration (ocd) 3: Over-current during steady operation (ocn) 4: Ground fault (GFF) 6: Over-current at stop (ocS) 7: Over-voltage during acceleration (ovA) 8: Over-voltage during deceleration (ovd) 9: Over-voltage during constant speed (ovn) 10: Over-voltage at stop (ovS) 11: Low-voltage during acceleration (LvA) 12: Low-voltage during deceleration (Lvd) 13: Low-voltage during constant speed (Lvn) 14: Low-voltage at stop (LvS) 15: Phase loss protection (orP) 16: IGBT overheating (oH1) 18: IGBT temperature detection failure (tH1o) 21: Over load (oL) 22: Electronic thermal relay 1 protection (EoL1) 23: Electronic thermal relay 2 protection (EoL2) 24: Motor PTC overheating (oH3) 26: Over torque 1 (ot1) 27: Over torque 2 (ot2) 28: Under current (uC) 31: EEPROM read error (cF2) 33: U-phase error (cd1) 34: V-phase error (cd2) 35: W-phase error (cd3) 36: cc (current clamp) hardware error (Hd0) 37: oc (over-current) hardware error (Hd1) 40: Auto-tuning error (AUE) 41: PID loss AI2 (AFE) 43: PG feedback loss (PGF2) 48: AI2 loss (ACE) 49: External fault (EF) 50: Emergency stop (EF1) 51: External Base Block (bb) 52: Password is locked (Pcod) 54: Illegal command (CE1) 55: Illegal data address (CE2) 56: Illegal data value (CE3) 57: Data is written to read-only address (CE4) 58: Modbus transmission time-out (CE10) | 61: Y-connection / fl-connection switch error (ydc) 62: Deceleration energy backup error (dEb) 63: Over slip error (oSL) 72: STO Loss (STL1) 76: STO (STo) 77: STO Loss 2 (STL2) 78: STO Loss 3 (STL3) 79: U-phase Over-current before run (Aoc) 80: V-phase Over-current before run (boc) 81: W-phase Over-current before run (coc) 82: Output phase loss U phase (oPL1) 83: Output phase loss V phase (oPL2) 84: Output phase loss W phase (oPL3) 87: Low frequency overload protection (oL3) 89: Rotor position detection error (roPd) 111: InrCOM time-out error (ictE) 121: Internal communication error (CP20) 123: Internal communication error (CP22) 124: Internal communication error (CP30) 126: Internal communication error (CP32) 127: Internal communication error (CP33) 128: Over-torque 3 (ot3) 129: Over-torque 4 (ot4) 134: Internal communication error (EoL3) 135: Internal communication error (EoL4) 140: Oc hardware error (Hd6) 141: GFF occurs before run (b4GFF) 142: Auto-tune error 1 (DC test stage) (AuE1) 143: Auto-tune error 2 (High frequency test stage) (AuE2) 144: Auto-tune error 3 (Rotary test stage) (AuE3) | R/W | 0 | 0-143
90 | P06 Protection | P6.32 | Second Most Recent Fault Record | Same as 6.31 | 0 | 290 | P06 Protection | P06.18 | Fault record 2 | See P06.17 for ranges. |  | R/W | 0 | 0-143
91 | P06 Protection | P6.33 | Third Most Recent Fault Record | Same as 6.31 | 0 | 291 | P06 Protection | P06.19 | Fault record 3 | See P06.17 for ranges. |  | R/W | 0 | 0-143
92 | P06 Protection | P6.34 | Fourth Most Recent Fault Record | Same as 6.31 | 0 | 292 | P06 Protection | P06.20 | Fault record 4 | See P06.17 for ranges. |  | R/W | 0 | 0-143
93 | P06 Protection | P6.35 | Fifth Most Recent Fault Record | Same as 6.31 | 0 | 293 | P06 Protection | P06.21 | Fault record 5 | See P06.17 for ranges. |  | R/W | 0 | 0-143
94 | P06 Protection | P6.36 | Sixth Most Recent Fault Record | Same as 6.31 | 0 | 294 | P06 Protection | P06.22 | Fault record 6 | See P06.17 for ranges. |  | R/W | 0 | 0-143
95 | P07 PID | P7.00 | Input Terminal for PID Feedback | 00: Inhibit PID operation 01: Forward-acting (heating loop) PID feedback, PV from AVI (0 to + 10V 02: Forward-acting (heating loop) PID feedback, PV from ACI (4 to 20mA) 03: Reverse-acting (cooling loop) PID feedback, PV from AVI (0 to +10V). 04: Reverse-acting (cooling loop) PID feedback, PV from ACI (4 to 20mA). | 0 | 389 | P08 Hi Func PID | P08.00 | Terminal selection of PID feedback | 0: No function 1: Negative PID feedback: by analog input (P03.00, P03.01) 2: Negative PID feedback: by single- phase input (DI7), without direction (P10.16=5) 4: Positive PID feedback: by analog input (P03.00, P03.01) 5: Positive PID feedback: by single- phase input (DI7), without direction (P10.16=5) 7: Negative PID feedback: by communication protocols 8: Positive PID feedback: by communication protocols |  | ♦R/W | 0 | 0-8
96 | P07 PID | P7.01 | PV 100% Value | 0.0 to 999 | 100 |  |  | xN/A
97 | P07 PID | P7.02 | PID Setpoint Source | 00: Keypad 01: Serial Communications | 0 | 419 | P08 Hi Func PID | P08.65 | PID target value source | 0: Frequency command (P00.20, P00.30) 1: P08.66 setting 2: RS-485 communication input 3: External analog input (refer to P03.00, P03.01) 6: Communication card 7: Digital keypad potentiometer dial (GS20 only) |  | ♦R/W | 0 | 0-7
98 | P07 PID | P7.10 | Keypad PID Setpoint | 0.0 to 999 | 0 | 720 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
99 | P07 PID | P7.11 | PID Multi-setpoint 1 | 0.0 to 999 | 0 | 721 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
100 | P07 PID | P7.12 | PID Multi-setpoint 2 | 0.0 to 999 | 0 | 722 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
101 | P07 PID | P7.13 | PID Multi-setpoint 3 | 0.0 to 999 | 0 | 723 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
102 | P07 PID | P7.14 | PID Multi-setpoint 4 | 0.0 to 999 | 0 | 724 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
103 | P07 PID | P7.15 | PID Multi-setpoint 5 | 0.0 to 999 | 0 | 725 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
104 | P07 PID | P7.16 | PID Multi-setpoint 6 | 0.0 to 999 | 0 | 726 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
105 | P07 PID | P7.17 | PID Multi-setpoint 7 | 0.0 to 999 | 0 | 727 |  | xN/A | Use onBoard PLC to move desired PID value when input signal is present
106 | P07 PID | P7.20 | Proportional Control | 0.0 to 10.0 | 1 | 390 | P08 Hi Func PID | P08.01 | Proportional gain (P) | 0.0-1000.0 (When P08.23 bit 1=0) 0.00-100.00 (When P08.23 bit 1=1) |  | ♦R/W | 1
107 | P07 PID | P7.21 | Integral Control | 0.00 to 100.0 sec | 1 | 391 | P08 Hi Func PID | P08.02 | Integral time (I) | 0.00-100.00 sec. |  | ♦R/W | 1
108 | P07 PID | P7.22 | Derivative Control | 0.00 to 1.00 sec | 0 | 392 | P08 Hi Func PID | P08.03 | Differential time (D) | 0.00-1.00 sec. |  | ♦R/W | 0
109 | P07 PID | P7.23 | Upper Bound for Integral Control | 00 to 100% | 100 | 393 | P08 Hi Func PID | P08.04 | Upper limit of integral control | 0.0-100.0% |  | ♦R/W | 100
110 | P07 PID | P7.24 | Derivative Filter Time Constant | 0.0 to 2.5 sec | 0 | 396 | P08 Hi Func PID | P08.07 | PID delay time | 0.0-2.5 sec. |  | ♦R/W | 0
111 | P07 PID | P7.25 | PID Output Frequency Limit | 00 to 110% | 100 | 394 | P08 Hi Func PID | P08.05 | PID output command limit (positive limit) | 0.0-110.0% |  | ♦R/W | 100
112 | P07 PID | P7.26 | Feedback Signal Detection Time | 0.0 to 3600 sec. | 60 | 397 | P08 Hi Func PID | P08.08 | Feedback signal detection time | 0.0-3600.0 sec. |  | ♦R/W | 0
113 | P07 PID | P7.27 | PID Feedback Loss | 00: Warn and AC Drive Stop 01: Warn and Continue Operation | 0 | 398 | P08 Hi Func PID | P08.09 | Feedback signal fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: Warn and operate at last frequency |  | ♦R/W | 0 | 0-3
114 | P08 Display | P8.00 | User Defined Display Function | 00: Output Frequency (Hz) 01: Motor Speed (RPM) 02: Output Freq. X P8.01 03: Output Current (A) 04: Motor Output Current (%) 05: Output Voltage (V) 06: DC Bus Voltage (V) 07: PID Setpoint 08: PID Feedback Signal (PV) 09: Frequency Setpoint | 0 | 5 | P00 Drive | P00.04 | User Display | 0: Output Amps (A) (unit: Amp) 1: Counter Value (c) (unit: CNT) 2: Output Frequency (H.) (unit: Hz) 3: DC Bus Voltage (V) (unit: VDC) 4: Output Voltage (E) (unit: VAC) 5: Power Factor (n) (unit: deg) 6: Output Power (P) (unit: kW) 7: Calculated RPM (r) (unit: rpm) 8: Est Output Torque (t) (unit: %) 10: PID Feedback (b) (unit: %) 11: AI1 Analog Input Signal (1.) (unit: %) 12: AI2 Analog Input Signal (2.) (unit: %) 14: IGBT Temperature (i.) (unit: 0C) 16: DI Input Status (ON / OFF) (i) 17: DO Output Status (ON / OFF) (o) 18: Multi-Speed Step (S) 19: CPU DI Input Status (d) 20: CPU DO Output Status (0.) 22: Pulse input frequency (S.) 25: Overload count (0.00-100.00%) (o.) (unit: %) 26: Ground fault GFF (G.) (unit: %) 27: DC bus voltage ripple (r.) (unit: VDC) 28: Display PLC register D1043 data (C) 30: Display the output of User-defined (U) 31: Display P00-05 user gain (K) 35: Control mode display 36: Present operating carrier frequency of the drive (J.) (Unit: Hz) 38: Display the drive status (6.) 39: Display the drive's estimated output torque, positive and negative, using N•m as unit (t 0.0: positive torque; -0.0: negative torque) (C.) 40: Torque command (L.) (unit: %) 41: kWh display (J) (unit: kWh) 42: PID target value (h.) (unit: %) 43: PID compensation (o.) (unit: %) 44: PID output frequency (b.) (unit: Hz) 46: Auxiliary frequency value (U.) (unit: Hz) 47: Master frequency value (A) (unit: Hz) 48: Frequency value after addition and subtraction of master and auxiliary frequency (L.) (unit: Hz) 51: PMSVC torque offset 58: P00.05 User gain display (K) (Does not display decimal places.) 62: I2t (o.) (unit: %) 63: Error code (E.) 64: Warning code (n.) 65: Accumulated motor operation record (day) (r.) (refer to P05.32) |  | ♦R/W | 3 | 0-44
115 | P08 Display | P8.01 | Frequency Scale Factor | 0.01 to 160.0 | 1 | 6 | P00 Drive | P00.05 | Coefficient Gain in Actual Output Frequency Display (H Page scale) | 0.00-160.00 |  | ♦R/W | 1
116 | P09 Communication | P9.00 | Communication Address | 01 to 254 | 1 | 431 | P09 Communication | P09.00 | Communication address | 1-254 |  | ♦R/W | 1
117 | P09 Communication | P9.01 | Transmission Speed | 00: 4800 baud 01: 9600 baud 02: 19200 baud 03: 38400 baud | 1 | 432 | P09 Communication | P09.01 | COM1 transmission speed | 4.8-115.2 Kbps |  | ♦R/W | 9.6 | 4.8-115.2 Kbps
118 | P09 Communication | P9.02 | Communication Protocol | 00: Modbus ASCII mode 7 data bits,no parity,2 stop bits 01: Modbus ASCII mode 7 data bits,even parity,1 stop bit 02: Modbus ASCII mode 7 data bits,odd parity,1 stop bit 03: Modbus RTU mode 8 data bits,no parity,2 stop bits 04: Modbus RTU mode 8 data bits,even parity,1 stop bit 05: Modbus RTU mode 8 data bits,odd parity,1 stop bit | 0 | 435 | P09 Communication | P09.04 | COM1 communication protocol | 1: 7, N, 2 (ASCII) 2: 7, E, 1 (ASCII) 3: 7, O, 1 (ASCII) 4: 7, E, 2 (ASCII) 5: 7, O, 2 (ASCII) 6: 8, N, 1 (ASCII) 7: 8, N, 2 (ASCII) 8: 8, E, 1 (ASCII) 9: 8, O, 1 (ASCII) 10: 8, E, 2 (ASCII) 11: 8, O, 2 (ASCII) 12: 8, N, 1 (RTU) 13: 8, N, 2 (RTU) 14: 8, E, 1 (RTU) 15: 8, O, 1 (RTU) 16: 8, E, 2 (RTU) 17: 8, O, 2 (RTU) |  | ♦R/W | 1
119 | P09 Communication | P9.03 | Transmission Fault Treatment | 00: Display fault and continue operating 01: Display fault and RAMP to stop 02: Display fault and COAST to stop 03: No fault displayed and continue operating | 0 | 433 | P09 Communication | P09.02 | COM1 transmission fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning, no fault, and continue operation |  | ♦R/W | 3
120 | P09 Communication | P9.04 | Time Out Detection | 00: Disable 01: Enable | 0 | 434 | P09 Communication | P09.03 | COM1 time-out detection | 0.0-100.0 sec. |  | ♦R/W | 0 | 0.0-100.0 sec.
121 | P09 Communication | P9.05 | Time Out Duration | 0.1 to 60.0 seconds | 0.5 | 436 | P09 Communication | P09.09 | Communication response delay time | 0.0-200.0 ms |  | ♦R/W | 2 | 0.0-200.0 ms
122 | P09 Communication | P9.07 | Parameter Lock | 00: All parameters can be set and read 01: All parameters are read-only | 0 | 3 | P00 Drive | P00.02 | Restore to Default | 0: No function 1: Parameter Lock 2: Convert to GS2 mode (Step 1 of 2) 3: Not used 4: Not used 5: Reset kWh Display to 0 6: Reset PLC 8: Disable Keypad Run 9: Reset all parameters to 50Hz defaults 10: Reset all parameters to 60Hz defaults 11: Reset all parameters to 50Hz defaults (retain user-defined parameter values P13.01~P13.50) 12: Reset all parameters to 60Hz defaults (retain user-defined parameter values P13.01~P13.50) 13: Not used 20: Convert to GS2 mode (Step 2 of 2) |  | R/W | 0
123 | P09 Communication | P9.08 | Restore to Default | 99: Restores all parameters to factory defaults | 0 | 3 | P00 Drive | P00.02 | Restore to Default | 0: No function 1: Parameter Lock 2: Convert to GS2 mode (Step 1 of 2) 3: Not used 4: Not used 5: Reset kWh Display to 0 6: Reset PLC 8: Disable Keypad Run 9: Reset all parameters to 50Hz defaults 10: Reset all parameters to 60Hz defaults 11: Reset all parameters to 50Hz defaults (retain user-defined parameter values P13.01~P13.50) 12: Reset all parameters to 60Hz defaults (retain user-defined parameter values P13.01~P13.50) 13: Not used 20: Convert to GS2 mode (Step 2 of 2) |  | R/W | 0
124 | P09 Communication | P9.11 | Block Transfer Parameter 1 | P0.00 to P8.01, P9.99 | P9.99 | 438 | P09 Communication | P09.11 | Block transfer 1 | 0-65535 |  | ♦R/W | 0
125 | P09 Communication | P9.12 | Block Transfer Parameter 2 | P0.00 to P8.01, P9.99 | P9.99 | 439 | P09 Communication | P09.12 | Block transfer 2 | 0-65535 |  | ♦R/W | 0
126 | P09 Communication | P9.13 | Block Transfer Parameter 3 | P0.00 to P8.01, P9.99 | P9.99 | 440 | P09 Communication | P09.13 | Block transfer 3 | 0-65535 |  | ♦R/W | 0
127 | P09 Communication | P9.14 | Block Transfer Parameter 4 | P0.00 to P8.01, P9.99 | P9.99 | 441 | P09 Communication | P09.14 | Block transfer 4 | 0-65535 |  | ♦R/W | 0
128 | P09 Communication | P9.15 | Block Transfer Parameter 5 | P0.00 to P8.01, P9.99 | P9.99 | 442 | P09 Communication | P09.15 | Block transfer 5 | 0-65535 |  | ♦R/W | 0
129 | P09 Communication | P9.16 | Block Transfer Parameter 6 | P0.00 to P8.01, P9.99 | P9.99 | 443 | P09 Communication | P09.16 | Block transfer 6 | 0-65535 |  | ♦R/W | 0
130 | P09 Communication | P9.17 | Block Transfer Parameter 7 | P0.00 to P8.01, P9.99 | P9.99 | 444 | P09 Communication | P09.17 | Block transfer 7 | 0-65535 |  | ♦R/W | 0
131 | P09 Communication | P9.18 | Block Transfer Parameter 8 | P0.00 to P8.01, P9.99 | P9.99 | 445 | P09 Communication | P09.18 | Block transfer 8 | 0-65535 |  | ♦R/W | 0
132 | P09 Communication | P9.19 | Block Transfer Parameter 9 | P0.00 to P8.01, P9.99 | P9.99 | 446 | P09 Communication | P09.19 | Block transfer 9 | 0-65535 |  | ♦R/W | 0
133 | P09 Communication | P9.20 | Block Transfer Parameter 10 | P0.00 to P8.01, P9.99 | P9.99 | 447 | P09 Communication | P09.20 | Block transfer 10 | 0-65535 |  | ♦R/W | 0
134 | P09 Communication | P9.21 | Block Transfer Parameter 11 | P0.00 to P8.01, P9.99 | P9.99 | 448 | P09 Communication | P09.21 | Block transfer 11 | 0-65535 |  | ♦R/W | 0
135 | P09 Communication | P9.22 | Block Transfer Parameter 12 | P0.00 to P8.01, P9.99 | P9.99 | 449 | P09 Communication | P09.22 | Block transfer 12 | 0-65535 |  | ♦R/W | 0
136 | P09 Communication | P9.23 | Block Transfer Parameter 13 | P0.00 to P8.01 | P9.99 | 450 | P09 Communication | P09.23 | Block transfer 13 | 0-65535 |  | ♦R/W | 0
137 | P09 Communication | P9.24 | Block Transfer Parameter 14 | P0.00 to P8.01 | P9.99 | 451 | P09 Communication | P09.24 | Block transfer 14 | 0-65535 |  | ♦R/W | 0
138 | P09 Communication | P9.25 | Block Transfer Parameter 15 | P0.00 to P8.01 | P9.99 | 452 | P09 Communication | P09.25 | Block transfer 15 | 0-65535 |  | ♦R/W | 0
139 | P09 Communication | P9.26 | Serial Comm Speed Reference | 0.0 to 400.0 Hz | 60 | 700 |  | xN/A | Use Command Write Word 2001H (see Parameter details for bit)
140 | P09 Communication | P9.27 | Serial Comm RUN Command | 00: Stop 01: Run | 0 | 701 |  | xN/A | Use Command Write Word 2000H (see Parameter details for bit)
141 | P09 Communication | P9.28 | Serial Comm Direction Command | 00: Forward 01: Reverse | 0 | 702 |  | xN/A | Use Command Write Word 2000H (see Parameter details for bit)
142 | P09 Communication | P9.29 | Serial Comm External Fault | 00: No fault 01: External fault | 0 | 703 |  | xN/A | Use Command Write Word 2001H (see Parameter details for bit)
143 | P09 Communication | P9.30 | Serial Comm Fault Reset | 00: No action 01: Fault Reset | 0 | 704 |  | xN/A | Use Command Write Word 2002H (see Parameter details for bit)
144 | P09 Communication | P9.31 | Serial Comm JOG Command | 00: Stop 01: Jog | 0 | 705 |  | xN/A | Use Command Write Word 2002H (see Parameter details for bit)
145 | P09 Communication | P9.39 | Firmware Version | #.## | #.## | 7 | P00 Drive | P00.06 | Firmware version | Read only |  | Read | ~
146 | P09 Communication | P9.41 | GS Series Number | 01: GS1 02: GS2 03: GS3 | ## |  |  | xN/A
147 | P09 Communication | P9.42 | Manufacturer Model Information | 00: GS2-20P5 (230V 1ph/3ph 0.5hp) 01: GS2-21P0 (230V 1ph/3ph 1hp) 02: GS2-22P0 (230V 1ph/3ph 2hp) 03: GS2-23P0 (230V 1ph/3ph 3hp) 04: GS2-25P0 (230V 3ph 5hp) 05: GS2-27P5 (230V 3ph 7.5hp) 06: Reserved 07: GS2-41P0 (460V 3ph 1hp) 08: GS2-42P0 (460V 3ph 2hp) 09: GS2-43P0 (460V 3ph 3hp) 10: GS2-45P0 (460V 3ph 5hp) 11: GS2-47P5 (460V 3ph 7.5hp) 12: GS2-4010 (460V 3ph 10hp) 13: GS2-10P2 (115V 1ph 0.25hp) 14: GS2-10P5 (115V 1ph 0.5hp) 15: GS2-11P0 (115V 1ph 1hp) 16~20: Reserved 21: GS2-51P0 (575V 3ph 1hp) 22: GS2-52P0 (575V 3ph 2hp) 23: GS2-53P0 (575V 3ph 3hp) 24: GS2-55P0 (575V 3ph 5hp) 25: GS2-57P5 (575V 3ph 7.5hp) 26: GS2-5010 (575V 3ph 10hp) | ## | 1 | P00 Drive | P00.00 | GS20 Model ID- Identity Code | 102: 120 V, 1 Phase, 0.25 HP 103: 120 V, 1 Phase, 0.5 HP 104: 120 V, 1 Phase, 1 HP 302: 230 V, 1 Phase, 0.25 HP 303: 230 V, 1 Phase, 0.5 HP 304: 230 V, 1 Phase, 1 HP 305: 230 V, 1 Phase, 2 HP 306: 230 V, 1 Phase, 3 HP 202: 230 V, 3 Phase, 0.25 HP 203: 230 V, 3 Phase, 0.5 HP 204: 230 V, 3 Phase, 1 HP 205: 230 V, 3 Phase, 2 HP 206: 230 V, 3 Phase, 3 HP 207: 230 V, 3 Phase, 5 HP 208: 230 V, 3 Phase, 7.5 HP 209: 230 V, 3 Phase, 10 HP 210: 230 V, 3 Phase, 15 HP 211: 230 V, 3 Phase, 20 HP 403: 460 V, 3 Phase, 0.5 HP 404: 460 V, 3 Phase, 1 HP 405: 460 V, 3 Phase, 2 HP 406: 460 V, 3 Phase, 3 HP 407: 460 V, 3 Phase, 5 HP 408: 460 V, 3 Phase, 7.5 HP 409: 460 V, 3 Phase, 10 HP 410: 460 V, 3 Phase, 15 HP 411: 460 V, 3 Phase, 20 HP 412: 460 V, 3 Phase, 25 HP 413: 460 V, 3 Phase, 30 HP 504: 575 V, 3 Phase, 1 HP 505: 575 V, 3 Phase, 2 HP 506: 575 V, 3 Phase, 3 HP 507: 575 V, 3 Phase, 5 HP 508: 575 V, 3 Phase, 7.5 HP 509: 575 V, 3 Phase, 10 HP |  | Read | ~

## GS20 only
DURAPULSE GS20 & GS20X PARAMETER SUMMARY
GS20 Seq | Parameter Group | Pr. No. | Parameter Description | Range | Range (con't) | R/W | Default | SEE DISCLAIMER
1 | P00 Drive | P00.00 | GS20 Model ID- Identity Code | 102: 120 V, 1 Phase, 0.25 HP 103: 120 V, 1 Phase, 0.5 HP 104: 120 V, 1 Phase, 1 HP 302: 230 V, 1 Phase, 0.25 HP 303: 230 V, 1 Phase, 0.5 HP 304: 230 V, 1 Phase, 1 HP 305: 230 V, 1 Phase, 2 HP 306: 230 V, 1 Phase, 3 HP 202: 230 V, 3 Phase, 0.25 HP 203: 230 V, 3 Phase, 0.5 HP 204: 230 V, 3 Phase, 1 HP 205: 230 V, 3 Phase, 2 HP 206: 230 V, 3 Phase, 3 HP 207: 230 V, 3 Phase, 5 HP 208: 230 V, 3 Phase, 7.5 HP 209: 230 V, 3 Phase, 10 HP 210: 230 V, 3 Phase, 15 HP 211: 230 V, 3 Phase, 20 HP | 403: 460 V, 3 Phase, 0.5 HP 404: 460 V, 3 Phase, 1 HP 405: 460 V, 3 Phase, 2 HP 406: 460 V, 3 Phase, 3 HP 407: 460 V, 3 Phase, 5 HP 408: 460 V, 3 Phase, 7.5 HP 409: 460 V, 3 Phase, 10 HP 410: 460 V, 3 Phase, 15 HP 411: 460 V, 3 Phase, 20 HP 412: 460 V, 3 Phase, 25 HP 413: 460 V, 3 Phase, 30 HP 504: 575 V, 3 Phase, 1 HP 505: 575 V, 3 Phase, 2 HP 506: 575 V, 3 Phase, 3 HP 507: 575 V, 3 Phase, 5 HP 508: 575 V, 3 Phase, 7.5 HP 509: 575 V, 3 Phase, 10 HP | Read | ~
2 | P00 Drive | P00.01 | Rated Current | Display by models |  | Read | ~
3 | P00 Drive | P00.02 | Restore to Default | 0: No function 1: Parameter Lock 2: Convert to GS2 mode (Step 1 of 2) 3: Not used 4: Not used 5: Reset kWh Display to 0 6: Reset PLC 8: Disable Keypad Run 9: Reset all parameters to 50Hz defaults 10: Reset all parameters to 60Hz defaults 11: Reset all parameters to 50Hz defaults (retain user-defined parameter values P13.01~P13.50) 12: Reset all parameters to 60Hz defaults (retain user-defined parameter values P13.01~P13.50) 13: Not used 20: Convert to GS2 mode (Step 2 of 2) |  | R/W | 0
4 | P00 Drive | P00.03 | Start-up display Selection | 0: F - Freq Setpoint 1: H - Output Hz 2: U - User Display P00-04) 3: A - Output Amps |  | ♦R/W | 0
5 | P00 Drive | P00.04 | User Display | 0: Output Amps (A) (unit: Amp) 1: Counter Value (c) (unit: CNT) 2: Output Frequency (H.) (unit: Hz) 3: DC Bus Voltage (V) (unit: VDC) 4: Output Voltage (E) (unit: VAC) 5: Power Factor (n) (unit: deg) 6: Output Power (P) (unit: kW) 7: Calculated RPM (r) (unit: rpm) 8: Est Output Torque (t) (unit: %) 10: PID Feedback (b) (unit: %) 11: AI1 Analog Input Signal (1.) (unit: %) 12: AI2 Analog Input Signal (2.) (unit: %) 14: IGBT Temperature (i.) (unit: 0C) 16: DI Input Status (ON / OFF) (i) 17: DO Output Status (ON / OFF) (o) 18: Multi-Speed Step (S) 19: CPU DI Input Status (d) 20: CPU DO Output Status (0.) 22: Pulse input frequency (S.) 25: Overload count (0.00-100.00%) (o.) (unit: %) 26: Ground fault GFF (G.) (unit: %) 27: DC bus voltage ripple (r.) (unit: VDC) 28: Display PLC register D1043 data (C) 30: Display the output of User-defined (U) 31: Display P00-05 user gain (K) 35: Control mode display 36: Present operating carrier frequency of the drive (J.) (Unit: Hz) 38: Display the drive status (6.) 39: Display the drive's estimated output torque, positive and negative, using N•m as unit (t 0.0: positive torque; -0.0: negative torque) (C.) 40: Torque command (L.) (unit: %) 41: kWh display (J) (unit: kWh) 42: PID target value (h.) (unit: %) 43: PID compensation (o.) (unit: %) 44: PID output frequency (b.) (unit: Hz) | 46: Auxiliary frequency value (U.) (unit: Hz) 47: Master frequency value (A) (unit: Hz) 48: Frequency value after addition and subtraction of master and auxiliary frequency (L.) (unit: Hz) 51: PMSVC torque offset 58: P00.05 User gain display (K) (Does not display decimal places.) 62: I2t (o.) (unit: %) 63: Error code (E.) 64: Warning code (n.) 65: Accumulated motor operation record (day) (r.) (refer to P05.32) | ♦R/W | 3
6 | P00 Drive | P00.05 | Coefficient Gain in Actual Output Frequency Display (H Page scale) | 0.00-160.00 |  | ♦R/W | 1
7 | P00 Drive | P00.06 | Firmware version | Read only |  | Read | ~
8 | P00 Drive | P00.07 | Parameter protection password input | 0-65535 0-4: the number of password attempts allowed |  | ♦R/W | 0
9 | P00 Drive | P00.08 | Parameter protection password setting | 0-65535 0: No password protection or password entered correctly (P00-07) 1: Parameter has been set |  | ♦R/W | 0
10 | P00 Drive | P00.10 | Control Method | 0: Speed Control mode 2: Torque mode |  | R/W | 0
11 | P00 Drive | P00.11 | Speed (Velocity) Control mode | 0: IMVF (V/F control) 1: IMVFPG (V/F control + encoder) 2: IM/PM SVC (IM or PM space vector control) 5: IMFOC Sensorless (field-oriented sensorless vector control) Note: For option 2 (SVC), see P05.33 for induction motor (IM) or permanent magnent (PM) motor selection. |  | R/W | 0
12 | P00 Drive | P00.16 | Torque duty selection | 0: Variable Torque (VT) 1: Constant Torque (CT) |  | R/W | 1
13 | P00 Drive | P00.17 | Carrier frequency | Variable Torque: 2-15 kHz Constant Torque: 2-15 kHz Note: When P00-11=5 (IMFOC Sensorless), the maximum setting value for the carrier frequency is 10 kHz. |  | R/W | 4
14 | P00 Drive | P00.19 | PLC command mask | bit 0: Control command is forced by PLC control bit 1: Frequency command is forced by PLC control bit 3: Torque command is forced by PLC control |  | Read | 0
15 | P00 Drive | P00.20 | Master frequency command source (AUTO, REMOTE) | 0: Digital keypad 1: RS-485 communication input 2: External analog input (Refer to P03.00) 3: External UP / DOWN terminal (digital input terminals) 4: Pulse input (DI7) without direction command (refer to P10.16 for pulse input config) 6: Not used 7: Digital keypad VR/potentiometer dial (GS20 only) 8: Communication card 9: PID controller Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0
16 | P00 Drive | P00.21 | Operation command source (AUTO, REMOTE) | 0: Digital keypad 1: External terminals 2: RS-485 communication input 3: Not used 5: Communication card Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function settings 41/42 or 56 or with GS4-KPD (optional) |  | ♦R/W | 0
17 | P00 Drive | P00.22 | Stop method | 0: Ramp to stop 1: Coast to stop |  | ♦R/W | 0
18 | P00 Drive | P00.23 | Motor direction control | 0: Enable forward / reverse 1: Disable reverse 2: Disable forward |  | ♦R/W | 0
19 | P00 Drive | P00.24 | Digital operator (keypad) frequency command memory | Read only |  | Read | 60
20 | P00 Drive | P00.25 | User-defined characteristics (COEFF ATT) | bit 0-3: user-defined decimal places 0000h-0000b: no decimal place 0001h-0001b: one decimal place 0002h-0010b: two decimal places 0003h-0011b: three decimal places bit 4-5: user-defined unit 000xh: Hz 001xh: rpm 002xh: % 003xh: kg 004xh: m/s 005xh: kW 006xh: HP 007xh: ppm 008xh: 1/m 009xh: kg/s 00Axh: kg/m 00Bxh: kg/h 00Cxh: lb/s 00Dxh: lb/m 00Exh: lb/h 00Fxh: ft/s 010xh: ft/m 011xh: m 012xh: ft 013xh: degC 014xh: degF 015xh: mbar 016xh: bar 017xh: Pa 018xh: kPa 019xh: mWG 01Axh: inWG 01Bxh: ftWG 01Cxh: psi 01Dxh: atm 01Exh: L/s 01Fxh: L/m 020xh: L/h 021xh: m3/s 022xh: m3/h 023xh: GPM 024xh: CFM |  | ♦R/W | 0
21 | P00 Drive | P00.26 | User-defined maximum value (COEFF MAX) | 0: Disable 0-65535 (when P00.25 is set to no decimal place) 0.0-6553.5 (when P00.25 is set to one decimal place) 0.00-655.35 (when P00.25 is set to two decimal places) 0.000-65.535 (when P00.25 is set to three decimal places) |  | RW | 0
22 | P00 Drive | P00.27 | User-defined value (COEFF SET) | Read only |  | Read | 0
23 | P00 Drive | P00.29 | LOCAL / REMOTE selection | 0: Standard HOA function 1: When switching between local and remote, the drive stops. 2: When switching between local and remote, the drive runs with REMOTE settings for frequency and operating status. 3: When switching between local and remote, the drive runs with LOCAL settings for frequency and operating status. 4: When switching between local and remote, the drive runs with LOCAL settings when switched to Local and runs with REMOTE settings when switched to Remote for frequency and operating status. |  | R/W | 4
24 | P00 Drive | P00.30 | Master frequency command source (HAND, LOCAL) | 0: Digital keypad 1: RS-485 communication input 2: External analog input (refer to P03.00) 3: External UP / DOWN terminal (digital input terminals) 4: Pulse input without direction command (refer to P10.16 for pulse input config) 6: Not used 7: Digital keypad VR/potentiometer dial (GS20 only) 8: Communication card 9: PID controller Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0
25 | P00 Drive | P00.31 | Operation command source (HAND, LOCAL) | 0: Digital keypad 1: External terminal 2: RS-485 communication input 3: Not used 5: Communication card Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0
26 | P00 Drive | P00.32 | Digital keypad STOP function | 0: STOP key disabled 1: STOP key enabled |  | ♦R/W | 0
27 | P00 Drive | P00.35 | Auxiliary frequency source | 0: Master and auxiliary frequency function disabled 1: Digital keypad 2: RS-485 communication input 3: Analog input 4: External UP / DOWN key input (digital input terminals) 5: Pulse input without direction command (refer to P10.16 for pulse input config) 6: Not used 7: Digital keypad VR/potentiometer dial (GS20 only) 8: Communication card |  | R/W | 0
28 | P00 Drive | P00.36 | Master and auxiliary frequency command selection | 0: Master + auxiliary frequency 1: Master - auxiliary frequency 2: Auxiliary - master frequency |  | R/W | 0
29 | P00 Drive | P00.48 | Display filter time (current) | 0.001-65.535 sec. |  | ♦R/W | 0.1
30 | P00 Drive | P00.49 | Display filter time (keypad) | 0.001-65.535 sec. |  | ♦R/W | 0.1
31 | P00 Drive | P00.50 | Date Code of Software version (date) | Read only |  | Read | 0
32 | P01 Basic | P01.00 | Maximum operation frequency | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
33 | P01 Basic | P01.01 | Motor 1 Fbase | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
34 | P01 Basic | P01.02 | Motor 1, Rated Voltage (Nameplate) | 120V / 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V 575V models: 0.0-637.0 V |  | R/W | 220.0 440.0 575.0
35 | P01 Basic | P01.03 | Motor 1, Mid-point frequency 1 | 0.00-599.00 Hz |  | R/W | 3
36 | P01 Basic | P01.04 | Motor 1, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 11.0 22.0 40.0
37 | P01 Basic | P01.05 | Motor 1, Mid-point frequency 2 | 0.00-599.00 Hz |  | R/W | 1.5
38 | P01 Basic | P01.06 | Motor 1, Mid-point voltage 2 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 5.0 10.0 26.1
39 | P01 Basic | P01.07 | Motor 1, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
40 | P01 Basic | P01.08 | Motor 1, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 1.0 2.0 16.7
41 | P01 Basic | P01.09 | Start-up frequency | 0.00-599.00 Hz |  | R/W | 0.5
42 | P01 Basic | P01.10 | Output frequency upper limit | 0.00-599.00 Hz |  | ♦R/W | 599
43 | P01 Basic | P01.11 | Output frequency lower limit | 0.00-599.00 Hz |  | ♦R/W | 0
44 | P01 Basic | P01.12 | Acceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
45 | P01 Basic | P01.13 | Deceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
46 | P01 Basic | P01.14 | Acceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
47 | P01 Basic | P01.15 | Deceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
48 | P01 Basic | P01.16 | Acceleration time 3 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
49 | P01 Basic | P01.17 | Deceleration time 3 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
50 | P01 Basic | P01.18 | Acceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
51 | P01 Basic | P01.19 | Deceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
52 | P01 Basic | P01.20 | JOG acceleration time | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
53 | P01 Basic | P01.21 | JOG deceleration time | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
54 | P01 Basic | P01.22 | JOG frequency | 0.00-599.00 Hz |  | ♦R/W | 6
55 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | 0.00-599.00 Hz |  | ♦R/W | 0
56 | P01 Basic | P01.24 | S-curve for acceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
57 | P01 Basic | P01.25 | S-curve for acceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
58 | P01 Basic | P01.26 | S-curve for deceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
59 | P01 Basic | P01.27 | S-curve for deceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2
60 | P01 Basic | P01.28 | Skip frequency 1 (upper limit) | 0.00-599.00 Hz |  | R/W | 0
61 | P01 Basic | P01.29 | Skip frequency 1 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
62 | P01 Basic | P01.30 | Skip frequency 2 (upper limit) | 0.00-599.00 Hz |  | R/W | 0
63 | P01 Basic | P01.31 | Skip frequency 2 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
64 | P01 Basic | P01.32 | Skip frequency 3 (upper limit) | 0.00-599.00 Hz |  | R/W | 0
65 | P01 Basic | P01.33 | Skip frequency 3 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
66 | P01 Basic | P01.34 | Zero-speed mode | 0: Output waiting 1: Zero-speed operation 2: Fmin (refer to P01.07 and P01.41) |  | R/W | 0
67 | P01 Basic | P01.35 | Motor 2, Output frequency (Base frequency / Motor's rated frequency) | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
68 | P01 Basic | P01.36 | Motor 2, Output voltage (Base voltage / Motor's rated voltage) | 120V / 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V 575V models: 0.0-637.0 V |  | R/W | 220.0 440.0 575.0
69 | P01 Basic | P01.37 | Motor 2, Mid-point frequency | 0.00-599.00 Hz |  | R/W | 3
70 | P01 Basic | P01.38 | Motor 2, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 11.0 22.0 40.0
71 | P01 Basic | P01.39 | Motor 2, Mid-point frequency 2 | 0.00-599.00 Hz |  | R/W | 1.5
72 | P01 Basic | P01.40 | Motor 2, Mid-point voltage 2 | 120V / 230V models: 0.0-240.0 V 460V models:0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 5.0 10.0 26.1
73 | P01 Basic | P01.41 | Motor 2, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
74 | P01 Basic | P01.42 | Motor 2, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 1.0 2.0 16.7
75 | P01 Basic | P01.43 | V/F curve selection | 0: V/F curve determined by P01.00-P01.08 1: V/F curve to the power of 1.5 2: V/F curve to the power of 2 |  | R/W | 0
76 | P01 Basic | P01.44 | Auto-acceleration and auto-deceleration setting | 0: Linear acceleration and deceleration 1: Auto-acceleration and linear deceleration 2: Linear acceleration and auto- deceleration 3: Auto-acceleration and auto- deceleration 4: Stall prevention by auto- acceleration and auto-deceleration (limited by P01.12 -P01.21) |  | ♦R/W | 0
77 | P01 Basic | P01.45 | Time unit for acceleration / deceleration and S-curve | 0: Unit 0.01 sec. 1: Unit 0.1 sec. |  | R/W | 0
78 | P01 Basic | P01.49 | Regenerative energy restriction control (decel method) | 0: Disable 1: Over voltage energy restriction 2: Traction energy control (TEC) |  | R/W | 0
79 | P01 Basic | P01.52 | Motor 2, Maximum operation frequency | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
80 | P01 Basic | P01.53 | Motor 3, Maximum operation frequency | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
81 | P01 Basic | P01.54 | Motor 3, Output frequency (Base frequency / Motor's rated frequency) | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
82 | P01 Basic | P01.55 | Motor 3, Output voltage (Base voltage / Motor's rated voltage) | 120V / 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V 575V models: 0.0-637.0 V |  | R/W | 220.0 440.0 575.0
83 | P01 Basic | P01.56 | Motor 3, Mid-point frequency 1 | 0.00-599.00 Hz |  | R/W | 3
84 | P01 Basic | P01.57 | Motor 3, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 11.0 22.0 40.0
85 | P01 Basic | P01.58 | Motor 3, Mid-point frequency 2 | 0.00-599.00 Hz |  | R/W | 1.5
86 | P01 Basic | P01.59 | Motor 3, Mid-point voltage 2 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 5.0 10.0 26.1
87 | P01 Basic | P01.60 | Motor 3, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
88 | P01 Basic | P01.61 | Motor 3, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 1.0 2.0 16.7
89 | P01 Basic | P01.62 | Motor 4, Maximum operation frequency | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
90 | P01 Basic | P01.63 | Motor 4, Output frequency (Base frequency / Motor's rated frequency) | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00
91 | P01 Basic | P01.64 | Motor 4, Output voltage (Base voltage / Motor's rated voltage) | 120V / 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V 575V models: 0.0-637.0 V |  | R/W | 220.0 440.0 575.0
92 | P01 Basic | P01.65 | Motor 4, Mid-point frequency 1 | 0.00-599.00 Hz |  | R/W | 3
93 | P01 Basic | P01.66 | Motor 4, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 11.0 22.0 40.0
94 | P01 Basic | P01.67 | Motor 4, Mid-point frequency 2 | 0.00-599.00 Hz |  | R/W | 1.5
95 | P01 Basic | P01.68 | Motor 4, Mid-point voltage 2 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 5.0 10.0 26.1
96 | P01 Basic | P01.69 | Motor 4, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
97 | P01 Basic | P01.70 | Motor 4, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V 575V models: 0.0-600.0 V |  | ♦R/W | 1.0 2.0 16.7
98 | P02 Digital IO | P02.00 | Two-wire / three- wire operation control | Note: On the drive, DI1 is labeled FWD, and DI2 is labeled REV. 0: No function 1: Two-wire mode 1, power on for operation control (DI1: FWD/STOP, DI2: REV/STOP) 2: Two-wire mode 2, power on for operation control (DI1: RUN/STOP, DI2: REV/FWD) 3: Three-wire, power on for operation control (DI1: RUN, DI2: REV/FWD, DI3: STOP) 4: Two-wire mode 1, Quick Start (DI1: FWD/STOP, DI2: REV/STOP) 5: Two-wire mode 2, Quick Start (DI1: RUN/STOP, DI2: REV/FWD) 6: Three-wire, Quick Start (DI1: RUN, DI2: REV/FWD, DI3: STOP) IMPORTANT 1) In the QuickStart function, terminal output remains in ready status, and the drive responds to the start command immediately. 2) When using the Quick Start function, output terminals U, V, and W are powered immediately. To avoid electric shock hazard, do not touch the terminals or modify the motor wiring. |  | R/W | 1
99 | P02 Digital IO | P02.01 | Multi-function input command 1 (FWD/DI1) | 0: No function 1: Multi-step speed command 1 / multi-step position command 1 2: Multi-step speed command 2 / multi-step position command 2 3: Multi-step speed command 3 / multi-step position command 3 4: Multi-step speed command 4 / multi-step position command 4 5: Reset 6: JOG [by external control or GS4- KPD (optional)] 7: Acceleration / deceleration speed inhibit 8: 1st and 2nd acceleration / deceleration time selection 9: 3rd and 4th acceleration / deceleration time selection 10: External Fault (EF) Input (P07.20) 11: Base Block (B.B.) input from external source 12: Output stop 13: Cancel the setting of auto- acceleration / auto-deceleration time 15: Rotating speed command from AI1 16: Rotating speed command from AI2 18: Force to stop (P07.20) 19: Digital up command 20: Digital down command 21: PID function disabled 22: Clear the counter 23: Input the counter value (DI6) 24: FWD JOG command 25: REV JOG command 26: TQC / Field Oriented Control (FOC) mode selection 27: ASR1 / ASR2 selection 28: Emergency stop (EF1) 29: Signal confirmation for Y-connection 30: Signal confirmation for ti. -connection 31: High torque bias (P11.30) 32: Middle torque bias (P11.31) 33: Low torque bias (P11.32) 38: Disable writing EEPROM function 39: Torque command direction 40: Force coasting to stop 41: HAND switch 42: AUTO switch 48: Mechanical gear ratio switch 49: Enable drive | 50: Slave dEb action to execute 51: Selection for PLC mode bit 0 52: Selection for PLC mode bit 1 56: Local / Remote selection 58: Enable fire mode (with RUN command) 59: Enable fire mode (without RUN command) 70: Force auxiliary frequency return to 0 71: Disable PID function, force PID output return to 0 72: Disable PID function, retain the output value before disabled 73: Force PID integral gain return to 0, disable integral 74: Reverse PID feedback 81: Simple positioning zero point position signal input 82: OOB loading balance detection 83: Multi-motor (IM) selection bit 0 84: Multi-motor (IM) selection bit 1 | R/W | 0
100 | P02 Digital IO | P02.02 | Multi-function input command 2 (REV/DI2) | See P02.01 for values. |  | R/W | 0
101 | P02 Digital IO | P02.03 | Multi-function input command 3 (DI3) | See P02.01 for values. |  | R/W | 1
102 | P02 Digital IO | P02.04 | Multi-function input command 4 (DI4) | See P02.01 for values. |  | R/W | 2
103 | P02 Digital IO | P02.05 | Multi-function input command 5 (DI5) | See P02.01 for values. |  | R/W | 3
104 | P02 Digital IO | P02.06 | Multi-function input command 6 (DI6) | See P02.01 for values. |  | R/W | 4
105 | P02 Digital IO | P02.07 | Multi-function input command 7 (DI7) | See P02.01 for values. For pulse input, use selection 0 - No function. |  | R/W | 0
106 | P02 Digital IO | P02.09 | UP / DOWN key mode | 0: UP / DOWN by the acceleration / deceleration time 1: UP / DOWN constant speed (P02.10) 2: Pulse signal (P02.10) 3: External terminals UP / DOWN mode |  | ♦R/W | 0
107 | P02 Digital IO | P02.10 | Constant speed, acceleration / deceleration speed of the UP/DOWN Key | 0.001-1.000 Hz/ms |  | ♦R/W | 0.001
108 | P02 Digital IO | P02.11 | Multi-function input response time | 0.000-30.000 sec. |  | ♦R/W | 0.005
109 | P02 Digital IO | P02.12 | Multi-function input mode selection | 0000h-FFFFh (0: N.O.; 1: N.C.) |  | ♦R/W | 0
110 | P02 Digital IO | P02.13 | Multi-function output 1 (R1) | 0: No function 1: Indication during RUN 2: Operation speed reached 3: Desired frequency reached 1 (P02.22) 4: Desired frequency reached 2 (P02.24) 5: Zero speed (Frequency command) 6: Zero speed including STOP (Frequency command) 7: Over-torque 1 (P06.06-06.08) 8: Over-torque 2 (P06.09-06.11) 9: Drive is ready 10: Low voltage warning (Lv) (P06.00) 11: Malfunction indication 13: Overheat warning (P06.15) 14: Software brake signal indicator (P07.00) 15: PID feedback error (P08.13, P08.14) 16: Slip error (oSL) 17: Count value reached, does not return to 0 (P02.20) 18: Count value reached, return to 0 (P02.19) 19: External interrupt B.B. input (Base Block) 20: Warning output 21: Over-voltage 22: Over-current stall prevention 23: Over-voltage stall prevention 24: Operation mode 25: Forward command 26: Reverse command 29: Output when frequency � P02.34 30: Output when frequency < P02.34 31: Y-connection for the motor coil 32: t.-connection for the motor coil 33: Zero speed (actual output frequency) 34: Zero speed including STOP (actual output frequency) 35: Error output selection 1 (P06.23) 36: Error output selection 2 (P06.24) 37: Error output selection 3 (P06.25) 38: Error output selection 4 (P06.26) 40: Speed reached (including STOP) 42: Crane function 43: Motor speed detection 44: Low current output (use with P06.71-06.73) 45: UVW output electromagnetic valve switch 46: Master dEb output | 51: Analog output control for RS-485 interface 52: Output control for communication cards 53: Fire mode indication 66: SO output logic A 67: Analog input level reached 68: SO output logic B 73: Over-torque 3 74: Over-torque 4 75: Forward RUN status 76: Reverse RUN status | ♦R/W | 11
111 | P02 Digital IO | P02.16 | Multi-function output 2 (DO1) | See P02.13 for values. |  | ♦R/W | 0
112 | P02 Digital IO | P02.17 | Multi-function output 3 (DO2) | See P02.13 for values. |  | ♦R/W | 0
113 | P02 Digital IO | P02.18 | Multi-function output direction ACT | 0000h-FFFFh (0: N.O.; 1: N.C.) |  | ♦R/W | 0000h
114 | P02 Digital IO | P02.19 | Terminal counting value reached (returns to 0) | 0-65500 |  | ♦R/W | 0
115 | P02 Digital IO | P02.20 | Preliminary (Middle) counting value reached (does not return to 0) | 0-65500 |  | ♦R/W | 0
116 | P02 Digital IO | P02.21 | Digital output gain (DO) | 1-55 |  | ♦R/W | 1
117 | P02 Digital IO | P02.22 | Desired frequency reached 1 | 0.00-599.00 Hz |  | ♦R/W | 60.00 / 50.00
118 | P02 Digital IO | P02.23 | The bandwidth of the desired frequency reached 1 | 0.00-599.00 Hz |  | ♦R/W | 2
119 | P02 Digital IO | P02.24 | Desired frequency reached 2 | 0.00-599.00 Hz |  | ♦R/W | 60.00 / 50.00
120 | P02 Digital IO | P02.25 | The bandwidth of the desired frequency reached 2 | 0.00-599.00 Hz |  | ♦R/W | 2
121 | P02 Digital IO | P02.34 | Output frequency setting for digital output terminal | 0.00-599.00 Hz (Motor speed when using PG Card) |  | ♦R/W | 0
122 | P02 Digital IO | P02.35 | External operation control selection after fault reset and reboot | 0: Disable 1: Drive runs if the RUN command remains after reset or reboot |  | ♦R/W | 0
123 | P02 Digital IO | P02.47 | Motor RPM zero- speed level | 0-65535 rpm |  | ♦R/W | 0
124 | P02 Digital IO | P02.50 | Display the status of multi-function input terminals DI1-DI7 | Monitor the status of multi-function input terminals |  | Read | 0
125 | P02 Digital IO | P02.51 | Display the status of multi-function output terminals R1, DO1, DO2 | Monitor the status of digital output terminals |  | Read | 0
126 | P02 Digital IO | P02.52 | Display the external multi-function input terminals DI1-DI7 used by PLC | Monitor the status of PLC input terminals |  | Read | 0
127 | P02 Digital IO | P02.53 | Display the external multi-function output terminals R1, DO1, DO2 used by PLC | Monitor the status of PLC output terminals |  | Read | 0
128 | P02 Digital IO | P02.54 | Display the frequency command executed by external terminal (EXT Speed REC) | 0.00-599.00 Hz (Read only) |  | Read | 0
129 | P02 Digital IO | P02.58 | Multi-function output terminal (function 42): brake frequency check point | 0.00-599.00 Hz |  | ♦R/W | 0
130 | P02 Digital IO | P02.78 | Motor deceleration gear ratio | 4.0-1000.0 |  | R/W | 200
131 | P02 Digital IO | P02.79 | Automatic index positioning angle setting | 0.0-6480.0 |  | R/W | 180
132 | P02 Digital IO | P02.80 | Automatic index positioning deceleration time | 0.00: Disable the function 0.01-100.00 sec. |  | ♦R/W | 0
133 | P02 Digital IO | P02.81 | EF activates when the terminal count value reached | 0: Terminal count value reached, no EF displays (continues to operate) 1: Terminal count value reached, EF activates |  | ♦R/W | 0
134 | P02 Digital IO | P02.82 | Initial Frequency com-mand (F) mode after stop | 0: Use current Frequency command 1: Use zero Frequency Command 2: Refer to P02.83 to set up |  | ♦R/W | 0
135 | P02 Digital IO | P02.83 | Initial Frequency com-mand (F) setting after stop | 0.00-599.00 Hz |  | ♦R/W | 60
136 | P03 Analog IO | P03.00 | Analog input selection (AI1) | 0: No function 1: Frequency command 2: Torque command (torque limit under speed mode) 3: Torque compensation command 4: PID target value 5: PID feedback signal 6: Thermistor (PTC) input value 7: Positive torque limit 8: Negative torque limit 9: Regenerative torque limit 10: Positive / negative torque limit 11: PT100 thermistor input value 12: Auxiliary frequency input 13: PID compensation value |  | ♦R/W | 1
137 | P03 Analog IO | P03.01 | Analog input selection (AI2) |  |  | ♦R/W | 0
138 | P03 Analog IO | P03.03 | Analog input bias (AI1) | -100.0-100.0% |  | ♦R/W | 0
139 | P03 Analog IO | P03.04 | Analog input bias (AI2) | -100.0-100.0% |  | ♦R/W | 0
140 | P03 Analog IO | P03.07 | Positive / negative bias mode (AI1) | 0: No bias 1: Lower than or equal to bias 2: Greater than or equal to bias 3: The absolute value of the bias voltage while serving as the center 4: Bias serves as the center |  | ♦R/W | 0
141 | P03 Analog IO | P03.08 | Positive / negative bias mode (AI2) |  |  | ♦R/W | 0
142 | P03 Analog IO | P03.10 | Reverse setting when analog signal input is negative frequency | 0: Negative frequency input is not allowed. The digital keypad or external terminal controls the forward and reverse direction. 1: Negative frequency input is allowed. Positive frequency = run in a forward direction; negative frequency = run in a reverse direction. The digital keypad or external terminal control cannot change the running direction. |  | ♦R/W | 0
143 | P03 Analog IO | P03.11 | Analog input gain (AI1) | -500.0-500.0% |  | ♦R/W | 100
144 | P03 Analog IO | P03.12 | Analog input gain (AI2) | -500.0-500.0% |  | ♦R/W | 100
145 | P03 Analog IO | P03.15 | Analog input filter (LPF) time (AI1) | 0.00-20.00 sec. |  | ♦R/W | 0.01
146 | P03 Analog IO | P03.16 | Analog input filter (LPF) time (AI2) | 0.00-20.00 sec. |  | ♦R/W | 0.01
147 | P03 Analog IO | P03.18 | Analog input addition function | 0: Disable (AI1, AI2) 1: Enable |  | ♦R/W | 0
148 | P03 Analog IO | P03.19 | Signal loss selection for analog input 4-20 mA | 0: Disable 1: Continue operation at the last frequency 2: Decelerate to 0 Hz 3: Stop immediately and display "ACE" |  | ♦R/W | 0
149 | P03 Analog IO | P03.20 | Multi-function output (A01) | 0: Output frequency (Hz) 1: Frequency command (Hz) 2: Motor speed (Hz) 3: Output current (rms) 4: Output voltage 5: DC bus voltage 6: Power factor 7: Power 8: Output torque 9: AI1 10: AI2 12: Iq current command 13: Iq feedback value 14: Id current command 15: Id feedback value 16: Vq-axis voltage command 17: Vd-axis voltage command 18: Torque command 19: PG2 (DI7) frequency command 21: RS-485 analog output 22: Communication card analog output 23: Constant voltage output |  | ♦R/W | 0
150 | P03 Analog IO | P03.21 | Analog output gain (A01) | 0.0-500.0% |  | ♦R/W | 100
151 | P03 Analog IO | P03.22 | Analog output in REV direction (A01) | 0: Absolute value in output voltage 1: Reverse output 0 V; forward output 0-10 V 2: Reverse output 5-0 V; forward output 5-10 V |  | ♦R/W | 0
152 | P03 Analog IO | P03.27 | A01 output bias | -100.00-100.00% |  | ♦R/W | 0
153 | P03 Analog IO | P03.28 | AI1 terminal input selection | 0: 0-10 V (only P03.63-P03.68 are valid) 3: -10-10 V (only P03.63-P03.74 are valid) |  | ♦R/W | 0
154 | P03 Analog IO | P03.29 | AI2 terminal input selection | 0: 4-20 mA 1: 0-10 V 2: 0-20 mA |  | ♦R/W | 0
155 | P03 Analog IO | P03.30 | PLC analog output terminal status | Monitor the status of the PLC analog output terminals bit 0: A01 status |  | Read | 0
156 | P03 Analog IO | P03.31 | A01 output selection | 0: 0-10 V output 1: 0-20 mA output 2: 4-20 mA output |  | ♦R/W | 0
157 | P03 Analog IO | P03.32 | A01 DC output setting level | 0.00-100.00% |  | ♦R/W | 0
158 | P03 Analog IO | P03.35 | A01 output filter time | 0.00-20.00 sec. |  | ♦R/W | 0.01
159 | P03 Analog IO | P03.39 | VR (keypad dial) input selection | 0: Disable 1: Frequency command |  | ♦R/W | 1
160 | P03 Analog IO | P03.40 | VR (keypad dial) input bias | -100.0-100.0% |  | ♦R/W | 0
161 | P03 Analog IO | P03.41 | VR (keypad dial) positive / negative bias | 0: No bias 1: Lower than or equal to bias 2: Greater than or equal to bias 3: The absolute value of the bias voltage while serving as the center 4: Bias serves as the center |  | ♦R/W | 0
162 | P03 Analog IO | P03.42 | VR (keypad dial) gain | -500.0-500.0% |  | ♦R/W | 100
163 | P03 Analog IO | P03.43 | VR (keypad dial) filter time | 0.00-2.00 sec. |  | ♦R/W | 0.01
164 | P03 Analog IO | P03.44 | Multi-function output (DO) by AI level source | 0: AI1 1: AI2 |  | ♦R/W | 0
165 | P03 Analog IO | P03.45 | AI upper level | -100-100% |  | ♦R/W | 50
166 | P03 Analog IO | P03.46 | AI lower level | -100-100% |  | ♦R/W | 10
167 | P03 Analog IO | P03.50 | Analog input curve calculation selection | 0: Normal curve 1: Three-point curve of AI1 2: Three-point curve of AI2 3: Three-point curve of AI1 & AI2 |  | ♦R/W | 0
168 | P03 Analog IO | P03.57 | AI2 lowest point | P03.29 = 1, 0.00-10.00 V P03.29 t 1, 0.00-20.00 mA |  | ♦R/W | 4
169 | P03 Analog IO | P03.58 | AI2 proportional lowest point | 0.00-100.00% |  | ♦R/W | 0
170 | P03 Analog IO | P03.59 | AI2 mid-point | P03.29 = 1, 0.00-10.00 V P03.29 t 1, 0.00-20.00 mA |  | ♦R/W | 12
171 | P03 Analog IO | P03.60 | AI2 proportional mid- point | 0.00-100.00% |  | ♦R/W | 50
172 | P03 Analog IO | P03.61 | AI2 highest point | P03.29 = 1, 0.00-10.00 V P03.29 t 1, 0.00-20.00 mA |  | ♦R/W | 20
173 | P03 Analog IO | P03.62 | AI2 proportional highest point | 0.00-100.00% |  | ♦R/W | 100
174 | P03 Analog IO | P03.63 | AI1 voltage lowest point | 0.00-10.00 V |  | ♦R/W | 0
175 | P03 Analog IO | P03.64 | AI1 proportional lowest point | -100.00-100.00% |  | ♦R/W | 0
176 | P03 Analog IO | P03.65 | AI1 voltage mid-point | 0.00-10.00 V |  | ♦R/W | 5
177 | P03 Analog IO | P03.66 | AI1 proportional mid- point | -100.00-100.00% |  | ♦R/W | 50
178 | P03 Analog IO | P03.67 | AI1 voltage highest point | 0.00-10.00 V |  | ♦R/W | 10
179 | P03 Analog IO | P03.68 | AI1 proportional highest point | -100.00-100.00% |  | ♦R/W | 100
180 | P03 Analog IO | P03.69 | Negative AI1 voltage highest point | -10.00-0.00 V (valid when P03.28 sets as -10-10 V) |  | ♦R/W | 0
181 | P03 Analog IO | P03.70 | Negative AI1 proportional highest point | -100.00-100.00% (valid when P03.28 sets as -10-10 V) |  | ♦R/W | 0
182 | P03 Analog IO | P03.71 | Negative AI1 voltage mid-point | -10.00-0.00 V (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -5
183 | P03 Analog IO | P03.72 | Negative AI1 proportional mid-point | -100.00-100.00% (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -50
184 | P03 Analog IO | P03.73 | Negative AI1 voltage lowest point | -10.00-0.00 V (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -10
185 | P03 Analog IO | P03.74 | Negative AI1 proportional lowest point | -100.00-100.00% (valid when P03.28 sets as -10-10 V) |  | ♦R/W | -100
186 | P04 Multi Step Spd | P04.00 | 1st step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
187 | P04 Multi Step Spd | P04.01 | 2nd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
188 | P04 Multi Step Spd | P04.02 | 3rd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
189 | P04 Multi Step Spd | P04.03 | 4th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
190 | P04 Multi Step Spd | P04.04 | 5th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
191 | P04 Multi Step Spd | P04.05 | 6th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
192 | P04 Multi Step Spd | P04.06 | 7th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
193 | P04 Multi Step Spd | P04.07 | 8th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
194 | P04 Multi Step Spd | P04.08 | 9th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
195 | P04 Multi Step Spd | P04.09 | 10th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
196 | P04 Multi Step Spd | P04.10 | 11th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
197 | P04 Multi Step Spd | P04.11 | 12th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
198 | P04 Multi Step Spd | P04.12 | 13th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
199 | P04 Multi Step Spd | P04.13 | 14th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
200 | P04 Multi Step Spd | P04.14 | 15th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0
201 | P04 Multi Step Spd | P04.50 | PLC buffer 0 | 0-65535 |  | ♦R/W | 0
202 | P04 Multi Step Spd | P04.51 | PLC buffer 1 | 0-65535 |  | ♦R/W | 0
203 | P04 Multi Step Spd | P04.52 | PLC buffer 2 | 0-65535 |  | ♦R/W | 0
204 | P04 Multi Step Spd | P04.53 | PLC buffer 3 | 0-65535 |  | ♦R/W | 0
205 | P04 Multi Step Spd | P04.54 | PLC buffer 4 | 0-65535 |  | ♦R/W | 0
206 | P04 Multi Step Spd | P04.55 | PLC buffer 5 | 0-65535 |  | ♦R/W | 0
207 | P04 Multi Step Spd | P04.56 | PLC buffer 6 | 0-65535 |  | ♦R/W | 0
208 | P04 Multi Step Spd | P04.57 | PLC buffer 7 | 0-65535 |  | ♦R/W | 0
209 | P04 Multi Step Spd | P04.58 | PLC buffer 8 | 0-65535 |  | ♦R/W | 0
210 | P04 Multi Step Spd | P04.59 | PLC buffer 9 | 0-65535 |  | ♦R/W | 0
211 | P04 Multi Step Spd | P04.60 | PLC buffer 10 | 0-65535 |  | ♦R/W | 0
212 | P04 Multi Step Spd | P04.61 | PLC buffer 11 | 0-65535 |  | ♦R/W | 0
213 | P04 Multi Step Spd | P04.62 | PLC buffer 12 | 0-65535 |  | ♦R/W | 0
214 | P04 Multi Step Spd | P04.63 | PLC buffer 13 | 0-65535 |  | ♦R/W | 0
215 | P04 Multi Step Spd | P04.64 | PLC buffer 14 | 0-65535 |  | ♦R/W | 0
216 | P04 Multi Step Spd | P04.65 | PLC buffer 15 | 0-65535 |  | ♦R/W | 0
217 | P04 Multi Step Spd | P04.66 | PLC buffer 16 | 0-65535 |  | ♦R/W | 0
218 | P04 Multi Step Spd | P04.67 | PLC buffer 17 | 0-65535 |  | ♦R/W | 0
219 | P04 Multi Step Spd | P04.68 | PLC buffer 18 | 0-65535 |  | ♦R/W | 0
220 | P04 Multi Step Spd | P04.69 | PLC buffer 19 | 0-65535 |  | ♦R/W | 0
221 | P05 Motor | P05.00 | Motor parameter auto-tuning | 0: No function 1: Dynamic test for induction motor (IM) 2: Static test for induction motor (IM) 5: Rolling auto-tuning for PM (IPM / SPM) 6: Simple rolling auto-tuning for induction motor (IM) 12: FOC sensorless inertia estimation 13: High frequency stall test for PM |  | R/W | 0
222 | P05 Motor | P05.01 | Induction Motor 1, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
223 | P05 Motor | P05.02 | Induction Motor 1, Rated power (kW) | 0.00-655.35 kW |  | ♦R/W | Model dependent
224 | P05 Motor | P05.03 | Induction Motor 1, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
225 | P05 Motor | P05.04 | Induction Motor 1, Number of poles | 2-20 |  | R/W | 4
226 | P05 Motor | P05.05 | Induction Motor 1, No-load amps | 0.00-P05.01 default |  | R/W | Model dependent
227 | P05 Motor | P05.06 | Induction Motor 1, Stator resistance (Rs) | 0.000-65.535 0 |  | R/W | Model dependent
228 | P05 Motor | P05.07 | Induction Motor 1, Rotor resistance (Rr) | 0.000-65.535 0 |  | R/W | 0
229 | P05 Motor | P05.08 | Induction Motor 1, Magnetizing inductance (Lm) | 0.0-6553.5 mH |  | R/W | 0
230 | P05 Motor | P05.09 | Induction Motor 1, Stator inductance (Lx) | 0.0-6553.5 mH |  | R/W | 0
231 | P05 Motor | P05.13 | Induction Motor 2, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
232 | P05 Motor | P05.14 | Induction Motor 2, Rated power (kW) | 0.00-655.35 kW |  | ♦R/W | Model dependent
233 | P05 Motor | P05.15 | Induction Motor 2, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
234 | P05 Motor | P05.16 | Induction Motor 2, Number of poles | 2-20 |  | R/W | 4
235 | P05 Motor | P05.17 | Induction Motor 2, No- load amps | 0.00-P05.13 default |  | R/W | Model dependent
236 | P05 Motor | P05.18 | Induction Motor 2, Stator resistance (Rs) | 0.000-65.535 0 |  | R/W | Model dependent
237 | P05 Motor | P05.19 | Induction Motor 2, Rotor resistance (Rr) | 0.000-65.535 0 |  | R/W | 0
238 | P05 Motor | P05.20 | Induction Motor 2, Magnetizing inductance (Lm) | 0.0-6553.5 mH |  | R/W | 0
239 | P05 Motor | P05.21 | Induction Motor 2, Stator inductance (Lx) | 0.0-6553.5 mH |  | R/W | 0
240 | P05 Motor | P05.22 | Multi-motor (induction) selection | 1: Motor 1 2: Motor 2 3: Motor 3 (VF or SVC control mode only) 4: Motor 4 (VF or SVC control mode only) |  | R/W | 1
241 | P05 Motor | P05.23 | Frequency for Y-connection / fl-connection switch for an induction motor | 0.00-599.00 Hz |  | ♦R/W | 60
242 | P05 Motor | P05.24 | Y-connection /fl-connection switch for an induction motor | 0: Disable 1: Enable |  | R/W | 0
243 | P05 Motor | P05.25 | Delay time for Y-connection /fl-connection switch for an induction motor | 0.000-60.000 sec. |  | ♦R/W | 0.2
244 | P05 Motor | P05.26 | Accumulated Watt- second for a motor in low word (W-msec.) | Read only |  | Read | 0
245 | P05 Motor | P05.27 | Accumulated Watt- second for a motor in high word (W-sec.) | Read only |  | Read | 0
246 | P05 Motor | P05.28 | Accumulated Watt- hour for a motor (W-hour) | Read only |  | Read | 0
247 | P05 Motor | P05.29 | Accumulated Watt- hour for a motor in low word (kW-hour) | Read only |  | Read | 0
248 | P05 Motor | P05.30 | Accumulated Watt- hour for a motor in high word (MW-hour) | Read only |  | Read | 0
249 | P05 Motor | P05.31 | Accumulated motor operation time (Minutes) | 0-1439 |  | R/W | 0
250 | P05 Motor | P05.32 | Accumulated motor operation time (days) | 0-65535 |  | R/W | 0
251 | P05 Motor | P05.33 | Induction motor (IM) or permanent magnet synchronous AC motor (PM) selection | 0: IM (Induction motor) 1: SPM (Surface permanent magnet synchronous AC motor) 2: IPM (Interior permanent magnet synchronous AC motor) |  | R/W | 0
252 | P05 Motor | P05.34 | Full-load current for a permanent magnet synchronous AC motor | 0-120% of the drive's rated current |  | R/W | Model dependent
253 | P05 Motor | P05.35 | Rated power for a permanent magnet synchronous AC motor | 0.00-655.35 kW |  | R/W | Model dependent
254 | P05 Motor | P05.36 | Rated speed for a permanent magnet synchronous AC motor | 0-65535 rpm |  | R/W | 2000
255 | P05 Motor | P05.37 | Number of poles for a permanent magnet synchronous AC motor | 0-65535 |  | R/W | 10
256 | P05 Motor | P05.39 | Stator resistance Rs for a permanent magnet synchronous AC motor | 0.000-65.535 0 |  | R/W | 0
257 | P05 Motor | P05.40 | Permanent magnet synchronous AC motor Ld | 0.00-655.35 mH |  | R/W | 0
258 | P05 Motor | P05.41 | Permanent magnet synchronous AC motor Lq | 0.00-655.35 mH |  | R/W | 0
259 | P05 Motor | P05.43 | Ke parameter of a permanent magnet synchronous AC motor | 0-65535 (Unit: V / krpm) |  | R/W | 0
260 | P05 Motor | P05.64 | Induction Motor 3, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
261 | P05 Motor | P05.65 | Induction Motor 3, Rated power (kW) | 0.00-655.35 kW |  | ♦R/W | Model dependent
262 | P05 Motor | P05.66 | Induction Motor 3, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
263 | P05 Motor | P05.67 | Induction Motor 3, Number of poles | 2-20 |  | R/W | 4
264 | P05 Motor | P05.68 | Induction Motor 3, No- load amps | 0.00-P05.64 default |  | R/W | Model dependent
265 | P05 Motor | P05.69 | Induction Motor 3, Stator resistance (Rs) | 0.000-65.535 0 |  | R/W | Model dependent
266 | P05 Motor | P05.70 | Induction Motor 4, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
267 | P05 Motor | P05.71 | Induction Motor 4, Rated power for (kW) | 0.00-655.35 kW |  | ♦R/W | Model dependent
268 | P05 Motor | P05.72 | Induction Motor 4, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
269 | P05 Motor | P05.73 | Induction Motor 4, Number of poles | 2-20 |  | R/W | 4
270 | P05 Motor | P05.74 | Induction Motor 4, No-load amps | 0.00-P05.70 default |  | R/W | Model dependent
271 | P05 Motor | P05.75 | Induction Motor 4, Stator resistance (Rs) | 0.000-65.535 0 |  | R/W | Model dependent
272 | P06 Protection | P06.00 | Low voltage level | 120V / 230V models: 150.0-220.0 VDC 460V models: 300.0-440.0 VDC 575V models: 375.0-550.0 VDC |  | ♦R/W | 180.0 360.0 450.0
273 | P06 Protection | P06.01 | Over-voltage stall prevention | 0: Disable 120V / 230V models: 0.0-390.0 VDC 460V models: 0.0-900.0 VDC 575V models: 0.0-1000.0 VDC |  | ♦R/W | 380.0 760.0 975.0
274 | P06 Protection | P06.02 | Selection for over-voltage stall prevention | 0: Traditional over-voltage stall prevention 1: Smart over-voltage stall prevention |  | ♦R/W | 0
275 | P06 Protection | P06.03 | Over-current stall prevention during acceleration (OCA) | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive) |  | ♦R/W | 180
276 | P06 Protection | P06.04 | Over-current stall prevention during operation (OCN) | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive) |  | ♦R/W | 180
277 | P06 Protection | P06.05 | Acceleration / deceleration time selection for stall prevention at constant speed | 0: By current acceleration / deceleration time 1: By the first acceleration / deceleration time 2: By the second acceleration / deceleration time 3: By the third acceleration / deceleration time 4: By the fourth acceleration / deceleration time 5: By Auto-acceleration / auto- deceleration |  | ♦R/W | 0
278 | P06 Protection | P06.06 | Over-torque detection selection (motor 1) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN |  | ♦R/W | 0
279 | P06 Protection | P06.07 | Over-torque detection level (motor 1) | 10-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 120
280 | P06 Protection | P06.08 | Over-torque detection time (motor 1) | 0.1-60.0 sec. |  | ♦R/W | 0.1
281 | P06 Protection | P06.09 | Over-torque detection selection (motor 2) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN |  | ♦R/W | 0
282 | P06 Protection | P06.10 | Over-torque detection level (motor 2) | 10-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 120
283 | P06 Protection | P06.11 | Over-torque detection time (motor 2) | 0.1-60.0 sec. |  | ♦R/W | 0.1
284 | P06 Protection | P06.12 | Current limit | 0-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 150
285 | P06 Protection | P06.13 | Electronic thermal relay selection 1 (motor 1) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with fan on the shaft) 2: Disabled |  | ♦R/W | 2
286 | P06 Protection | P06.14 | Electronic thermal relay action time 1 (motor 1) | 30.0-600.0 sec. |  | ♦R/W | 60
287 | P06 Protection | P06.15 | Temperature level overheat (OH) warning | 0.0-110.00C |  | ♦R/W | Model dependent
288 | P06 Protection | P06.16 | Stall prevention limit level (Weak magnetic field current stall prevention level) | 0-100% (refer to P06.03-P06.04) |  | ♦R/W | 100
289 | P06 Protection | P06.17 | Fault record 1 | 0: No fault record 1: Over-current during acceleration (ocA) 2: Over-current during deceleration (ocd) 3: Over-current during steady operation (ocn) 4: Ground fault (GFF) 6: Over-current at stop (ocS) 7: Over-voltage during acceleration (ovA) 8: Over-voltage during deceleration (ovd) 9: Over-voltage during constant speed (ovn) 10: Over-voltage at stop (ovS) 11: Low-voltage during acceleration (LvA) 12: Low-voltage during deceleration (Lvd) 13: Low-voltage during constant speed (Lvn) 14: Low-voltage at stop (LvS) 15: Phase loss protection (orP) 16: IGBT overheating (oH1) 18: IGBT temperature detection failure (tH1o) 21: Over load (oL) 22: Electronic thermal relay 1 protection (EoL1) 23: Electronic thermal relay 2 protection (EoL2) 24: Motor PTC overheating (oH3) 26: Over torque 1 (ot1) 27: Over torque 2 (ot2) 28: Under current (uC) 31: EEPROM read error (cF2) 33: U-phase error (cd1) 34: V-phase error (cd2) 35: W-phase error (cd3) 36: cc (current clamp) hardware error (Hd0) 37: oc (over-current) hardware error (Hd1) 40: Auto-tuning error (AUE) 41: PID loss AI2 (AFE) 43: PG feedback loss (PGF2) 48: AI2 loss (ACE) 49: External fault (EF) 50: Emergency stop (EF1) 51: External Base Block (bb) 52: Password is locked (Pcod) 54: Illegal command (CE1) 55: Illegal data address (CE2) 56: Illegal data value (CE3) 57: Data is written to read-only address (CE4) 58: Modbus transmission time-out (CE10) | 61: Y-connection / fl-connection switch error (ydc) 62: Deceleration energy backup error (dEb) 63: Over slip error (oSL) 72: STO Loss (STL1) 76: STO (STo) 77: STO Loss 2 (STL2) 78: STO Loss 3 (STL3) 79: U-phase Over-current before run (Aoc) 80: V-phase Over-current before run (boc) 81: W-phase Over-current before run (coc) 82: Output phase loss U phase (oPL1) 83: Output phase loss V phase (oPL2) 84: Output phase loss W phase (oPL3) 87: Low frequency overload protection (oL3) 89: Rotor position detection error (roPd) 111: InrCOM time-out error (ictE) 121: Internal communication error (CP20) 123: Internal communication error (CP22) 124: Internal communication error (CP30) 126: Internal communication error (CP32) 127: Internal communication error (CP33) 128: Over-torque 3 (ot3) 129: Over-torque 4 (ot4) 134: Internal communication error (EoL3) 135: Internal communication error (EoL4) 140: Oc hardware error (Hd6) 141: GFF occurs before run (b4GFF) 142: Auto-tune error 1 (DC test stage) (AuE1) 143: Auto-tune error 2 (High frequency test stage) (AuE2) 144: Auto-tune error 3 (Rotary test stage) (AuE3) | R/W | 0
290 | P06 Protection | P06.18 | Fault record 2 | See P06.17 for ranges. |  | R/W | 0
291 | P06 Protection | P06.19 | Fault record 3 | See P06.17 for ranges. |  | R/W | 0
292 | P06 Protection | P06.20 | Fault record 4 | See P06.17 for ranges. |  | R/W | 0
293 | P06 Protection | P06.21 | Fault record 5 | See P06.17 for ranges. |  | R/W | 0
294 | P06 Protection | P06.22 | Fault record 6 | See P06.17 for ranges. |  | R/W | 0
295 | P06 Protection | P06.23 | Fault output option 1 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
296 | P06 Protection | P06.24 | Fault output option 2 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
297 | P06 Protection | P06.25 | Fault output option 3 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
298 | P06 Protection | P06.26 | Fault output option 4 | 0-65535 (refer to bit table for fault code) |  | ♦R/W | 0
299 | P06 Protection | P06.27 | Electronic thermal relay selection 2 (motor 2) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with fan on the shaft) 2: Disabled |  | ♦R/W | 2
300 | P06 Protection | P06.28 | Electronic thermal relay action time 2 (motor 2) | 30.0-600.0 sec. |  | ♦R/W | 60
301 | P06 Protection | P06.29 | PTC detection selection | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning |  | ♦R/W | 0
302 | P06 Protection | P06.30 | PTC level | 0.0-100.0% |  | ♦R/W | 50
303 | P06 Protection | P06.31 | Frequency command at malfunction | 0.00-599.00 Hz |  | Read | 0
304 | P06 Protection | P06.32 | Output frequency at malfunction | 0.00-599.00 Hz |  | Read | 0
305 | P06 Protection | P06.33 | Output voltage at malfunction | 0.0-6553.5 V |  | Read | 0
306 | P06 Protection | P06.34 | DC bus voltage at malfunction | 0.0-6553.5 V |  | Read | 0
307 | P06 Protection | P06.35 | Output current at malfunction | 0.00-655.35 Amp |  | Read | 0
308 | P06 Protection | P06.36 | IGBT temperature at malfunction | -3276.7-3276.70C |  | Read | 0
309 | P06 Protection | P06.38 | Motor speed at malfunction | -32767-32767 rpm |  | Read | 0
310 | P06 Protection | P06.39 | Torque command at malfunction | -32767-32767% |  | Read | 0
311 | P06 Protection | P06.40 | Status of the digital input terminal at malfunction | 0000h-FFFFh |  | Read | 0
312 | P06 Protection | P06.41 | Status of the digital output terminal at malfunction | 0000h-FFFFh |  | Read | 0
313 | P06 Protection | P06.42 | Drive status at malfunction | 0000h-FFFFh |  | Read | 0
314 | P06 Protection | P06.44 | STO latch selection | 0: STO latch 1: STO no latch |  | ♦R/W | 0
315 | P06 Protection | P06.45 | Output phase loss detection action (OPHL) | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning |  | ♦R/W | 3
316 | P06 Protection | P06.46 | Detection time for output phase loss | 0.000-65.535 sec. |  | ♦R/W | 0.5
317 | P06 Protection | P06.47 | Current detection level for output phase loss | 0.00-100.00% |  | ♦R/W | 1
318 | P06 Protection | P06.48 | DC brake time for output phase loss | 0.000-65.535 sec. |  | ♦R/W | 0
319 | P06 Protection | P06.49 | LvX auto-reset | 0: Disable 1: Enable |  | R/W | 0
320 | P06 Protection | P06.53 | Input phase loss detection action (OrP) | 0: Fault and ramp to stop 1: Fault and coast to stop |  | ♦R/W | 0
321 | P06 Protection | P06.55 | Derating protection | 0: Constant rated current and limit carrier frequency by load current and temperature 1: Constant carrier frequency and limit load current by setting carrier frequency 2: Constant rated current (same as setting 0), but close current limit |  | ♦R/W | 0
322 | P06 Protection | P06.56 | PT100 voltage level 1 | 0.000-10.000 V |  | ♦R/W | 5
323 | P06 Protection | P06.57 | PT100 voltage level 2 | 0.000-10.000 V |  | ♦R/W | 7
324 | P06 Protection | P06.58 | PT100 level 1 frequency protection | 0.00-599.00 Hz |  | ♦R/W | 0
325 | P06 Protection | P06.59 | PT100 activation level 1 protection frequency delay time | 0-6000 sec. |  | ♦R/W | 60
326 | P06 Protection | P06.60 | Software detection GFF current level | 0.0-6553.5% |  | ♦R/W | 60
327 | P06 Protection | P06.61 | Software detection GFF filter time | 0.00-655.35 sec. |  | ♦R/W | 0.1
328 | P06 Protection | P06.63 | Operation time of fault record 1 (Days) | 0-65535 days |  | Read | 0
329 | P06 Protection | P06.64 | Operation time of fault record 1 (Minutes) | 0-1439 min. |  | Read | 0
330 | P06 Protection | P06.65 | Operation time of fault record 2 (Days) | 0-65535 days |  | Read | 0
331 | P06 Protection | P06.66 | Operation time of fault record 2 (Minutes) | 0-1439 min. |  | Read | 0
332 | P06 Protection | P06.67 | Operation time of fault record 3 (Days) | 0-65535 days |  | Read | 0
333 | P06 Protection | P06.68 | Operation time of fault record 3 (Minutes) | 0-1439 min. |  | Read | 0
334 | P06 Protection | P06.69 | Operation time of fault record 4 (Days) | 0-65535 days |  | Read | 0
335 | P06 Protection | P06.70 | Operation time of fault record 4 (Minutes) | 0-1439 min. |  | Read | 0
336 | P06 Protection | P06.71 | Low current setting level | 0.0-100.0% |  | ♦R/W | 0
337 | P06 Protection | P06.72 | Low current detection time | 0.00-360.00 sec. |  | ♦R/W | 0
338 | P06 Protection | P06.73 | Low current action | 0: No function 1: Fault and coast to stop 2: Fault and ramp to stop by the second deceleration time 3: Warn and continue operation |  | ♦R/W | 0
339 | P06 Protection | P06.80 | Fire mode | 0: Disable 1: Operates in a counterclockwise direction 2: Operates in a clockwise direction |  | R/W | 0
340 | P06 Protection | P06.81 | Operating frequency in fire mode | 0.00-599.00 Hz |  | ♦R/W | 60
341 | P06 Protection | P06.88 | Operation times in fire mode | 0-65535 times |  | Read | 0
342 | P06 Protection | P06.90 | Operation time of fault record 5 (days) | 0-65535 days |  | Read | 0
343 | P06 Protection | P06.91 | Operation time of fault record 5 (Minutes) | 0-1439 min. |  | Read | 0
344 | P06 Protection | P06.92 | Operation time of fault record 6 (days) | 0-65535 days |  | Read | 0
345 | P06 Protection | P06.93 | Operation time of fault record 6 (Minutes) | 0-1439 min. |  | Read | 0
346 | P07 Special | P07.00 | Software brake chopper threshold level | 120V / 230V models: 350.0-450.0 VDC 460V models: 700.0-900.0 VDC 575V models: 875.0-1000.0 VDC |  | ♦R/W | 370.0 740.0 950.0
347 | P07 Special | P07.01 | DC brake current level | 0-100% |  | ♦R/W | 0
348 | P07 Special | P07.02 | DC brake time at start-up | 0.0-60.0 sec. |  | ♦R/W | 0
349 | P07 Special | P07.03 | DC brake time at STOP | 0.0-60.0 sec. |  | ♦R/W | 0
350 | P07 Special | P07.04 | DC brake frequency at STOP | 0.00-599.00 Hz |  | ♦R/W | 0
351 | P07 Special | P07.05 | Voltage increasing gain | 1-200% |  | ♦R/W | 100
352 | P07 Special | P07.06 | Restart after momentary power loss | 0: Stop operation 1: Speed tracking by the speed before the power loss 2: Speed tracking by the minimum output frequency |  | ♦R/W | 0
353 | P07 Special | P07.07 | Allowed power loss duration | 0.0-20.0 sec. |  | ♦R/W | 2
354 | P07 Special | P07.08 | Base Block time | 0.0-60.0 sec. |  | ♦R/W | 0.5
355 | P07 Special | P07.09 | Current limit of speed tracking | 20-200% |  | ♦R/W | 100
356 | P07 Special | P07.10 | Restart after fault action | 0: Stop operation 1: Speed tracking by current speed 2: Speed tracking by minimum output frequency |  | ♦R/W | 0
357 | P07 Special | P07.11 | Number of times of restart after fault | 0-10 |  | ♦R/W | 0
358 | P07 Special | P07.12 | Speed tracking during start-up | 0: Disable 1: Speed tracking by the maximum output frequency 2: Speed tracking by the motor frequency at start-up 3: Speed tracking by the minimum output frequency |  | ♦R/W | 0
359 | P07 Special | P07.13 | dEb function selection | 0: Disable 1: dEb with auto-acceleration / auto- deceleration, the drive does not output the frequency after the power is restored. 2: dEb with auto-acceleration / auto- deceleration, the drive outputs the frequency after the power is restored. 3: dEb low-voltage control, then the drive's voltage increases to 350 VDC / 700 VDC and ramps to stop after low frequency 4: dEb high-voltage control of 350 VDC / 700 VDC, and the drive ramps to stop |  | ♦R/W | 0
360 | P07 Special | P07.15 | Dwell time at acceleration | 0.00-600.00 sec. |  | ♦R/W | 0
361 | P07 Special | P07.16 | Dwell frequency at acceleration | 0.00-599.00 Hz |  | ♦R/W | 0
362 | P07 Special | P07.17 | Dwell time at deceleration | 0.00-600.00 sec. |  | ♦R/W | 0
363 | P07 Special | P07.18 | Dwell frequency at deceleration | 0.00-599.00 Hz |  | ♦R/W | 0
364 | P07 Special | P07.19 | Fan cooling control | 0: Fan is always ON 1: Fan is OFF after the AC motor drive stops for one minute. 2: Fan is ON when the AC motor drive runs, fan is OFF when the AC motor drive stops. 3: Fan turns ON when temperature (IGBT) reaches approx 600C. |  | ♦R/W | 3
365 | P07 Special | P07.20 | Emergency stop (EF) & force to stop selection | 0: Coast to stop 1: Stop by the first deceleration time 2: Stop by the second deceleration time 3: Stop by the third deceleration time 4: Stop by the fourth deceleration time 5: System deceleration 6: Automatic deceleration |  | ♦R/W | 0
366 | P07 Special | P07.21 | Automatic energy- saving setting | 0: Disable 1: Enable |  | ♦R/W | 0
367 | P07 Special | P07.22 | Energy-saving gain | 10-1000% |  | ♦R/W | 100
368 | P07 Special | P07.23 | Automatic voltage regulation (AVR) function | 0: Enable AVR 1: Disable AVR 2: Disable AVR during deceleration |  | ♦R/W | 0
369 | P07 Special | P07.24 | Torque command filter time (V/F and SVC control mode) | 0.001-10.000 sec. |  | ♦R/W | 0.05
370 | P07 Special | P07.25 | Slip compensation filter time (V/F and SVC control mode) | 0.001-10.000 sec. |  | ♦R/W | 0.1
371 | P07 Special | P07.26 | Torque compensation gain (V/F and SVC control mode) | IM: 0-10 (when P05.33 = 0) PM: 0-5000 (when P05.33 = 1 or 2) |  | ♦R/W | 1
372 | P07 Special | P07.27 | Slip compensation gain (V/F and SVC control mode) | 0.00-10.00 |  | ♦R/W | 0.00 (Default value is 1.00 in SVC mode)
373 | P07 Special | P07.29 | Slip deviation level | 0.0-100.0% 0: No detection |  | ♦R/W | 0
374 | P07 Special | P07.30 | Over-slip deviation detection time | 0.0-10.0 sec. |  | ♦R/W | 1
375 | P07 Special | P07.31 | Over-slip deviation treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning |  | ♦R/W | 0
376 | P07 Special | P07.32 | Motor oscillation compensation factor | 0-10000 |  | ♦R/W | 1000
377 | P07 Special | P07.33 | Auto-restart interval of fault | 0.0-6000.0 sec. |  | ♦R/W | 60
378 | P07 Special | P07.38 | PMSVC voltage feed forward gain | 0.50-2.00 |  | R/W | 1
379 | P07 Special | P07.46 | OOB sampling time | 0.1-120.0 sec. |  | R/W | 1
380 | P07 Special | P07.47 | Number of OOB sampling times | 00-32 |  | R/W | 20
381 | P07 Special | P07.48 | OOB average sampling angle | Read only |  | Read | 0
382 | P07 Special | P07.62 | dEb gain (Kp) | 0-65535 |  | ♦R/W | 8000
383 | P07 Special | P07.71 | Torque compensation gain (motor 2) | IM: 0-10 (when P05.33 = 0) PM: 0-5000 (when P05.33 = 1 or 2) |  | ♦R/W | 1
384 | P07 Special | P07.72 | Slip compensation gain (motor 2) | 0.00-10.00 |  | ♦R/W | 0.00 (Default value is 1.00 in SVC mode)
385 | P07 Special | P07.73 | Torque compensation gain (motor 3) | IM: 0-10 (when P05.33 = 0) PM: 0-5000 (when P05.33 = 1 or 2) |  | ♦R/W | 1
386 | P07 Special | P07.74 | Slip compensation gain (motor 3) | 0.00-10.00 |  | ♦R/W | 0.00 (Default value is 1.00 in SVC mode)
387 | P07 Special | P07.75 | Torque compensation gain (motor 4) | IM: 0-10 (when P05.33 = 0) PM: 0-5000 (when P05.33 = 1 or 2) |  | ♦R/W | 1
388 | P07 Special | P07.76 | Slip compensation gain (motor 4) | 0.00-10.00 |  | ♦R/W | 0.00 (Default value is 1.00 in SVC mode)
389 | P08 Hi Func PID | P08.00 | Terminal selection of PID feedback | 0: No function 1: Negative PID feedback: by analog input (P03.00, P03.01) 2: Negative PID feedback: by single- phase input (DI7), without direction (P10.16=5) 4: Positive PID feedback: by analog input (P03.00, P03.01) 5: Positive PID feedback: by single- phase input (DI7), without direction (P10.16=5) 7: Negative PID feedback: by communication protocols 8: Positive PID feedback: by communication protocols |  | ♦R/W | 0
390 | P08 Hi Func PID | P08.01 | Proportional gain (P) | 0.0-1000.0 (When P08.23 bit 1=0) 0.00-100.00 (When P08.23 bit 1=1) |  | ♦R/W | 1
391 | P08 Hi Func PID | P08.02 | Integral time (I) | 0.00-100.00 sec. |  | ♦R/W | 1
392 | P08 Hi Func PID | P08.03 | Differential time (D) | 0.00-1.00 sec. |  | ♦R/W | 0
393 | P08 Hi Func PID | P08.04 | Upper limit of integral control | 0.0-100.0% |  | ♦R/W | 100
394 | P08 Hi Func PID | P08.05 | PID output command limit (positive limit) | 0.0-110.0% |  | ♦R/W | 100
395 | P08 Hi Func PID | P08.06 | PID feedback value by communication protocol | -200.00-200.00% |  | ♦R/W | 0
396 | P08 Hi Func PID | P08.07 | PID delay time | 0.0-2.5 sec. |  | ♦R/W | 0
397 | P08 Hi Func PID | P08.08 | Feedback signal detection time | 0.0-3600.0 sec. |  | ♦R/W | 0
398 | P08 Hi Func PID | P08.09 | Feedback signal fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: Warn and operate at last frequency |  | ♦R/W | 0
399 | P08 Hi Func PID | P08.10 | Sleep frequency | 0.00-599.00 Hz |  | ♦R/W | 0
400 | P08 Hi Func PID | P08.11 | Wake-up frequency | 0.00-599.00 Hz |  | ♦R/W | 0
401 | P08 Hi Func PID | P08.12 | Sleep time | 0.0-6000.0 sec. |  | ♦R/W | 0
402 | P08 Hi Func PID | P08.13 | PID feedback signal error deviation level | 1.0-50.0% |  | ♦R/W | 10
403 | P08 Hi Func PID | P08.14 | PID feedback signal error deviation detection time | 0.1-300.0 sec. |  | ♦R/W | 5
404 | P08 Hi Func PID | P08.15 | PID feedback signal filter time | 0.1-300.0 sec. |  | ♦R/W | 5
405 | P08 Hi Func PID | P08.16 | PID compensation selection | 0: Parameter setting 1: Analog input |  | ♦R/W | 0
406 | P08 Hi Func PID | P08.17 | PID compensation | -100.0-100.0% |  | ♦R/W | 0
407 | P08 Hi Func PID | P08.18 | Sleep mode function setting | 0: Refer to PID output command 1: Refer to PID feedback signal |  | R/W | 0
408 | P08 Hi Func PID | P08.19 | Wake-up integral limit | 0.0-200.0% |  | ♦R/W | 50
409 | P08 Hi Func PID | P08.20 | PID mode selection | 0: Serial connection 1: Parallel connection |  | R/W | 0
410 | P08 Hi Func PID | P08.21 | Enable PID to change the operation direction | 0: Operation direction cannot be changed 1: Operation direction can be changed |  | R/W | 0
411 | P08 Hi Func PID | P08.22 | Wake-up delay time | 0.00-600.00 sec. |  | ♦R/W | 0
412 | P08 Hi Func PID | P08.23 | PID control flag | bit 0 = 1: PID running in reverse follows the setting for P00.23. bit 0 = 0: PID running in reverse refers to PID's calculated value. bit 1 = 1: two decimal places for PID Kp bit 1 = 0: one decimal place for PID Kp |  | ♦R/W | 2
413 | P08 Hi Func PID | P08.26 | PID output command limit (reverse limit) | 0.0-100.0% |  | ♦R/W | 100
414 | P08 Hi Func PID | P08.27 | Acceleration / deceleration time for PID command | 0.00-655.35 sec. |  | ♦R/W | 0
415 | P08 Hi Func PID | P08.29 | Frequency base corresponding to 100.00% PID | 0: PID control output 100.00% corresponding to maximum operation frequency (P01.00) 1: PID control output 100.00% corresponding to the input value of the auxiliary frequency |  | ♦R/W | 0
416 | P08 Hi Func PID | P08.31 | Proportional gain 2 | 0.0-1000.0 (when P08.23 setting bit1=0) 0.00-100.00 (when P08.23 setting bit1=1) |  | ♦R/W | 1
417 | P08 Hi Func PID | P08.32 | Integral time 2 | 0.00-100.00 sec. |  | ♦R/W | 1
418 | P08 Hi Func PID | P08.33 | Differential time 2 | 0.00-1.00 sec. |  | ♦R/W | 0
419 | P08 Hi Func PID | P08.65 | PID target value source | 0: Frequency command (P00.20, P00.30) 1: P08.66 setting 2: RS-485 communication input 3: External analog input (refer to P03.00, P03.01) 6: Communication card 7: Digital keypad potentiometer dial (GS20 only) |  | ♦R/W | 0
420 | P08 Hi Func PID | P08.66 | PID target value setting | -100.00-100.00% |  | ♦R/W | 50
421 | P08 Hi Func PID | P08.67 | Master and auxiliary reverse running cutoff frequency | 0.0-100.0% |  | ♦R/W | 10
422 | P08 Hi Func PID | P08.68 | PID deviation limit | 0.00-100.00% |  | ♦R/W | 0
423 | P08 Hi Func PID | P08.69 | Integral separation level | 0.00-100.00% |  | ♦R/W | 0
424 | P08 Hi Func PID | P08.70 | Smart start-up level | 0.00-100.00% |  | R/W | 5
425 | P08 Hi Func PID | P08.71 | Smart start-up frequency command | 0.00-599.00 Hz |  | ♦R/W | 0
426 | P08 Hi Func PID | P08.72 | Smart start-up acceleration time | 0.00-600.00 sec. |  | ♦R/W | 3
427 | P08 Hi Func PID | P08.75 | PID2 parameter switch condition | 0: No switching (refer to P08.01-P08.03) 1: Auto-switch based on the output frequency 2: Auto-switch based on the deviation |  | ♦R/W | 0
428 | P08 Hi Func PID | P08.76 | PID2 parameter switch deviation 1 | 0.00-P08.77% |  | ♦R/W | 10
429 | P08 Hi Func PID | P08.77 | PID2 parameter switch deviation 2 | P08.76-100.00% |  | ♦R/W | 40
430 | P08 Hi Func PID | P08.78 | Allowed reverse running time after start-up | 0.0-6553.5 sec. |  | ♦R/W | 0
431 | P09 Communication | P09.00 | Communication address | 1-254 |  | ♦R/W | 1
432 | P09 Communication | P09.01 | COM1 transmission speed | 4.8-115.2 Kbps |  | ♦R/W | 9.6
433 | P09 Communication | P09.02 | COM1 transmission fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning, no fault, and continue operation |  | ♦R/W | 3
434 | P09 Communication | P09.03 | COM1 time-out detection | 0.0-100.0 sec. |  | ♦R/W | 0
435 | P09 Communication | P09.04 | COM1 communication protocol | 1: 7, N, 2 (ASCII) 2: 7, E, 1 (ASCII) 3: 7, O, 1 (ASCII) 4: 7, E, 2 (ASCII) 5: 7, O, 2 (ASCII) 6: 8, N, 1 (ASCII) 7: 8, N, 2 (ASCII) 8: 8, E, 1 (ASCII) 9: 8, O, 1 (ASCII) 10: 8, E, 2 (ASCII) 11: 8, O, 2 (ASCII) 12: 8, N, 1 (RTU) 13: 8, N, 2 (RTU) 14: 8, E, 1 (RTU) 15: 8, O, 1 (RTU) 16: 8, E, 2 (RTU) 17: 8, O, 2 (RTU) |  | ♦R/W | 1
436 | P09 Communication | P09.09 | Communication response delay time | 0.0-200.0 ms |  | ♦R/W | 2
437 | P09 Communication | P09.10 | Communication main frequency | 0.00-599.00 Hz |  | R/W | 60
438 | P09 Communication | P09.11 | Block transfer 1 | 0-65535 |  | ♦R/W | 0
439 | P09 Communication | P09.12 | Block transfer 2 | 0-65535 |  | ♦R/W | 0
440 | P09 Communication | P09.13 | Block transfer 3 | 0-65535 |  | ♦R/W | 0
441 | P09 Communication | P09.14 | Block transfer 4 | 0-65535 |  | ♦R/W | 0
442 | P09 Communication | P09.15 | Block transfer 5 | 0-65535 |  | ♦R/W | 0
443 | P09 Communication | P09.16 | Block transfer 6 | 0-65535 |  | ♦R/W | 0
444 | P09 Communication | P09.17 | Block transfer 7 | 0-65535 |  | ♦R/W | 0
445 | P09 Communication | P09.18 | Block transfer 8 | 0-65535 |  | ♦R/W | 0
446 | P09 Communication | P09.19 | Block transfer 9 | 0-65535 |  | ♦R/W | 0
447 | P09 Communication | P09.20 | Block transfer 10 | 0-65535 |  | ♦R/W | 0
448 | P09 Communication | P09.21 | Block transfer 11 | 0-65535 |  | ♦R/W | 0
449 | P09 Communication | P09.22 | Block transfer 12 | 0-65535 |  | ♦R/W | 0
450 | P09 Communication | P09.23 | Block transfer 13 | 0-65535 |  | ♦R/W | 0
451 | P09 Communication | P09.24 | Block transfer 14 | 0-65535 |  | ♦R/W | 0
452 | P09 Communication | P09.25 | Block transfer 15 | 0-65535 |  | ♦R/W | 0
453 | P09 Communication | P09.26 | Block transfer 16 | 0-65535 |  | ♦R/W | 0
454 | P09 Communication | P09.30 | Communication decoding method | 0: Decoding method 1 1: Decoding method 2 |  | R/W | 1
455 | P09 Communication | P09.33 | PLC command force to 0 | 0-65535 |  | ♦R/W | 0
456 | P09 Communication | P09.35 | PLC address | 1-254 |  | R/W | 2
457 | P09 Communication | P09.60 | Communication card identification | 0: No communication card 4: Modbus-TCP slave 5: EtherNet/IP slave 10: Backup power supply |  | Read | 0
458 | P09 Communication | P09.61 | Firmware version of communication card | Read only |  | Read | 0
459 | P09 Communication | P09.62 | Product code | Read only |  | Read | 0
460 | P09 Communication | P09.63 | Error code | Read only |  | Read | 0
461 | P09 Communication | P09.74 | Set Comm Master Protocol | 0: Ethernet IP and Modbus TCP both 1: Ethernet IP 2: Modbus TCP |  | ♦R/W | 1
462 | P09 Communication | P09.75 | Communication card IP configuration (Ethernet) | 0: Static IP 1: Dynamic IP (DHCP) |  | ♦R/W | 0
463 | P09 Communication | P09.76 | Communication card IP address 1 (Ethernet) | 0-255 |  | ♦R/W | 0
464 | P09 Communication | P09.77 | Communication card IP address 2 (Ethernet) | 0-255 |  | ♦R/W | 0
465 | P09 Communication | P09.78 | Communication card IP address 3 (Ethernet) | 0-255 |  | ♦R/W | 0
466 | P09 Communication | P09.79 | Communication card IP address 4 (Ethernet) | 0-255 |  | ♦R/W | 0
467 | P09 Communication | P09.80 | Communication card address mask 1 (Ethernet) | 0-255 |  | ♦R/W | 0
468 | P09 Communication | P09.81 | Communication card address mask 2 (Ethernet) | 0-255 |  | ♦R/W | 0
469 | P09 Communication | P09.82 | Communication card address mask 3 (Ethernet) | 0-255 |  | ♦R/W | 0
470 | P09 Communication | P09.83 | Communication card address mask 4 (Ethernet) | 0-255 |  | ♦R/W | 0
471 | P09 Communication | P09.84 | Communication card gateway address 1 (Ethernet) | 0-255 |  | ♦R/W | 0
472 | P09 Communication | P09.85 | Communication card gateway address 2 (Ethernet) | 0-255 |  | ♦R/W | 0
473 | P09 Communication | P09.86 | Communication card gateway address 3 (Ethernet) | 0-255 |  | ♦R/W | 0
474 | P09 Communication | P09.87 | Communication card gateway address 4 (Ethernet) | 0-255 |  | ♦R/W | 0
475 | P09 Communication | P09.88 | Communication card password (low word) (Ethernet) | 0-99 |  | ♦R/W | 0
476 | P09 Communication | P09.89 | Communication card password (high word) (Ethernet) | 0-99 |  | ♦R/W | 0
477 | P09 Communication | P09.90 | Reset communication card (Ethernet) | 0: Disable 1: Reset to defaults |  | ♦R/W | 0
478 | P09 Communication | P09.91 | Additional settings for the communication card (Ethernet) | bit 0: Enable IP filter bit 1: Enable internet parameters (1 bit) When the IP address is set, this bit is enabled. After updating the parameters for the communication card, this bit changes to disabled. bit 2: Enable login password (1 bit) When you enter the login password, this bit is enabled. After updating the communication card parameters, this bit changes to disabled. |  | ♦R/W | 0
479 | P09 Communication | P09.92 | Communication card status (Ethernet) | bit 0: Enable password When the communication card is set with a password, this bit is enabled. When the password is cleared, this bit is disabled. |  | R/W | 0
480 | P09 Communication | P09.93 | ENETIP Comm Card Fault Select | 0: Warn & Continue Operation 1: Warn & Ramp to Stop 2: Warn & Coast to Stop 3: No Warning & Continue Operation |  | ♦R/W | 3
481 | P09 Communication | P09.94 | ENETIP Comm Card Time Out Detection | 0: Disable 1: Enable |  | ♦R/W | 1
482 | P09 Communication | P09.95 | ENETIP Comm Card Time Out Duration | 0.1 to 100.0 seconds |  | ♦R/W | 3
483 | P10 Spd Fdbk Control | P10.00 | Encoder type selection | 0: Disabled 5: Pulse input (DI7) |  | R/W | 0
484 | P10 Spd Fdbk Control | P10.01 | Encoder pulses per revolution | 1-20000 |  | R/W | 600
485 | P10 Spd Fdbk Control | P10.02 | Encoder input type setting | 0: Disable 5: Single-phase input (DI7) |  | R/W | 0
486 | P10 Spd Fdbk Control | P10.04 | Electrical gear at load side A1 | 1-65535 |  | ♦R/W | 100
487 | P10 Spd Fdbk Control | P10.05 | Electrical gear at motor side B1 | 1-65535 |  | ♦R/W | 100
488 | P10 Spd Fdbk Control | P10.06 | Electrical gear at load side A2 | 1-65535 |  | ♦R/W | 100
489 | P10 Spd Fdbk Control | P10.07 | Electrical gear at motor side B2 | 1-65535 |  | ♦R/W | 100
490 | P10 Spd Fdbk Control | P10.10 | Encoder stall level | 0: No function 0-120% |  | ♦R/W | 115
491 | P10 Spd Fdbk Control | P10.11 | Detection time of encoder stall | 0.0-2.0 sec. |  | ♦R/W | 0.1
492 | P10 Spd Fdbk Control | P10.12 | Encoder stall action | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop |  | ♦R/W | 2
493 | P10 Spd Fdbk Control | P10.13 | Encoder slip range | 0: Disable 0-50% |  | ♦R/W | 50
494 | P10 Spd Fdbk Control | P10.14 | Detection time of encoder slip | 0.0-10.0 sec. |  | ♦R/W | 0.5
495 | P10 Spd Fdbk Control | P10.15 | Encoder stall and slip error action | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop |  | ♦R/W | 2
496 | P10 Spd Fdbk Control | P10.16 | Pulse input type setting | 0: Disabled 5: Single-phase input (DI7) |  | ♦R/W | 0
497 | P10 Spd Fdbk Control | P10.17 | Electrical gear A | 1-65535 |  | ♦R/W | 100
498 | P10 Spd Fdbk Control | P10.18 | Electrical gear B | 1-65535 |  | ♦R/W | 100
499 | P10 Spd Fdbk Control | P10.21 | PG2 (DI7) pulse input speed command low pass filter time | 0.000-65.535 sec. |  | ♦R/W | 0.1
500 | P10 Spd Fdbk Control | P10.24 | FOC & TQC function control | 0-65535 |  | ♦R/W | 0
501 | P10 Spd Fdbk Control | P10.25 | FOC bandwidth for speed observer | 20.0-100.0 Hz |  | ♦R/W | 40
502 | P10 Spd Fdbk Control | P10.26 | FOC minimum stator frequency | 0.0-10.0% fN |  | ♦R/W | 2
503 | P10 Spd Fdbk Control | P10.27 | FOC low pass filter time constant | 1-1000 ms |  | ♦R/W | 50
504 | P10 Spd Fdbk Control | P10.28 | FOC gain for excitation current rise time | 33-100% Tr |  | ♦R/W | 100
505 | P10 Spd Fdbk Control | P10.29 | Upper limit of frequency deviation | 0.00-200.00 Hz |  | ♦R/W | 20
506 | P10 Spd Fdbk Control | P10.31 | I/F mode, current command | 0-150% rated current of the motor |  | ♦R/W | 40
507 | P10 Spd Fdbk Control | P10.32 | PM sensorless speed estimator bandwidth | 0.00-600.00 Hz |  | ♦R/W | 5
508 | P10 Spd Fdbk Control | P10.34 | PM sensorless speed estimator low-pass filter gain | 0.00-655.35 |  | ♦R/W | 1
509 | P10 Spd Fdbk Control | P10.35 | Active Magnetic Regulator (AMR) (Kp) gain | 0.00-3.00 |  | ♦R/W | 1
510 | P10 Spd Fdbk Control | P10.36 | Active Magnetic Regulator (AMR) (Ki) gain | 0.00-3.00 |  | ♦R/W | 0.2
511 | P10 Spd Fdbk Control | P10.39 | Frequency point to switch from I/F mode to PM sensorless mode | 0.00-599.00 Hz |  | ♦R/W | 20
512 | P10 Spd Fdbk Control | P10.42 | Initial angle detection pulse value | 0.0-3.0 |  | ♦R/W | 1
513 | P10 Spd Fdbk Control | P10.49 | Zero voltage time during start-up | 0.000-60.000 sec. |  | ♦R/W | 0
514 | P10 Spd Fdbk Control | P10.51 | Injection frequency | 0-1200 Hz |  | ♦R/W | 500
515 | P10 Spd Fdbk Control | P10.52 | Injection magnitude | 120V / 230V models: 100.0 V 460V models: 200.0 V 575V models: 200.0 V Note: The setting range varies depending on the voltage. |  | ♦R/W | 15.0 30.0 37.5
516 | P10 Spd Fdbk Control | P10.53 | Angle detection method | 0: Disabled 1: Force attracting the rotor to zero degrees 2: High frequency injection 3: Pulse injection |  | ♦R/W | 0
517 | P11 Advanced | P11.00 | System control | bit 0: Auto-tuning for ASR bit 3: Dead time compensation closed bit 7: Save or do not save the frequency |  | R/W | 0
518 | P11 Advanced | P11.01 | Per-unit of system inertia | 1-65535 (256 = 1 PU) |  | R/W | 256
519 | P11 Advanced | P11.02 | ASR1/ASR2 switch frequency | 5.00-599.00 Hz |  | ♦R/W | 7
520 | P11 Advanced | P11.03 | ASR1 low-speed bandwidth | 1-40 Hz |  | Read | 0
521 | P11 Advanced | P11.04 | ASR2 high-speed bandwidth | 1-40 Hz |  | Read | 0
522 | P11 Advanced | P11.05 | Zero-speed bandwidth | 1-40 Hz |  | Read | 0
523 | P11 Advanced | P11.06 | ASR1 (Kp) gain | 0-40 Hz |  | ♦R/W | 10
524 | P11 Advanced | P11.07 | ASR1 (Ki) integral time | 0.000-10.000 sec. |  | ♦R/W | 0.1
525 | P11 Advanced | P11.08 | ASR2 (Kp) gain | 0-40 Hz |  | ♦R/W | 10
526 | P11 Advanced | P11.09 | ASR2 (Ki) integral time | 0.000-10.000 sec. |  | ♦R/W | 0.1
527 | P11 Advanced | P11.10 | ASR Kp gain of zero speed | 0-40 Hz |  | ♦R/W | 10
528 | P11 Advanced | P11.11 | ASR (Ki) integral time of zero speed | 0.000-10.000 sec. |  | ♦R/W | 0.1
529 | P11 Advanced | P11.12 | Gain for ASR speed feed forward | 0-200% |  | ♦R/W | 0
530 | P11 Advanced | P11.13 | PDFF gain value | 0-200% |  | ♦R/W | 30
531 | P11 Advanced | P11.14 | ASR output low pass filter time | 0.000-0.350 sec. |  | ♦R/W | 0.008
532 | P11 Advanced | P11.15 | Notch filter depth | 0-20 db |  | ♦R/W | 0
533 | P11 Advanced | P11.16 | Notch filter frequency | 0.00-200.00 Hz |  | ♦R/W | 0
534 | P11 Advanced | P11.17 | Forward motor torque limit | 0-500% |  | ♦R/W | 500
535 | P11 Advanced | P11.18 | Forward regenerative torque limit | 0-500% |  | ♦R/W | 500
536 | P11 Advanced | P11.19 | Reverse motor torque limit | 0-500% |  | ♦R/W | 500
537 | P11 Advanced | P11.20 | Reverse regenerative torque limit | 0-500% |  | ♦R/W | 500
538 | P11 Advanced | P11.21 | Flux weakening curve for motor 1 gain value | 0-200% |  | ♦R/W | 90
539 | P11 Advanced | P11.22 | Flux weakening curve for motor 2 gain value | 0-200% |  | ♦R/W | 90
540 | P11 Advanced | P11.23 | Flux weakening area speed response | 0-150% |  | ♦R/W | 65
541 | P11 Advanced | P11.27 | Maximum torque command | 0-500% |  | ♦R/W | 100
542 | P11 Advanced | P11.28 | Torque offset source | 0: Disable 1: Analog signal input 2: RS-485 communication (P11.29) 3: Controlled through external terminals (P11.30-P11.32) |  | ♦R/W | 0
543 | P11 Advanced | P11.29 | Torque offset setting | -100.0-100.0% |  | ♦R/W | 0
544 | P11 Advanced | P11.30 | High torque offset | -100.0-100.0% |  | ♦R/W | 30
545 | P11 Advanced | P11.31 | Middle torque offset | -100.0-100.0% |  | ♦R/W | 20
546 | P11 Advanced | P11.32 | Low torque offset | -100.0-100.0% |  | ♦R/W | 10
547 | P11 Advanced | P11.33 | Torque command source | 0: Digital keypad 1: RS-485 communication (P11.34) 2: Analog signal input (P03.00) 5: Communication Card |  | ♦R/W | 0
548 | P11 Advanced | P11.34 | Torque command | -100.0-100.0% |  | ♦R/W | 0
549 | P11 Advanced | P11.35 | Torque command filter time | 0.000-1.000 sec. |  | ♦R/W | 0
550 | P11 Advanced | P11.36 | Speed limit selection | 0: Set by P11.37 (forward speed limit) and P11.38 (reverse speed limit) 1: Set by P00.20 (Master frequency command (AUTO, REMOTE) source) and P11.37, P11.38 2: Set by P00.20 (master frequency command (AUTO, REMOTE) source) |  | R/W | 0
551 | P11 Advanced | P11.37 | Forward speed limit (Torque mode) | 0-120% |  | ♦R/W | 10
552 | P11 Advanced | P11.38 | Reverse speed limit (Torque mode) | 0-120% |  | ♦R/W | 10
553 | P11 Advanced | P11.41 | PWM mode selection | 0: Two-phase modulation mode 2: Space vector modulation mode |  | R/W | 2
554 | P11 Advanced | P11.42 | System control flag | 0000-FFFFh |  | ♦R/W | 0
555 | P13 Macro/User | P13.00 | Industry-specific parameter application | 00: Disabled 01: User-defined parameter 02: Compressor 03: Fan 04: Pump 05: Conveyor 06: Machine tool 07: Packing 08: Textiles 10: Logistics 11: Tension PID 12: Tension PID + master / auxiliary frequency |  | R/W | 0
556 | P13 Macro/User | P13.01 | User-defined parameter
557 | P13 Macro/User | P13.02 | User-defined parameter
558 | P13 Macro/User | P13.03 | User-defined parameter
559 | P13 Macro/User | P13.04 | User-defined parameter
560 | P13 Macro/User | P13.05 | User-defined parameter
561 | P13 Macro/User | P13.06 | User-defined parameter
562 | P13 Macro/User | P13.07 | User-defined parameter
563 | P13 Macro/User | P13.08 | User-defined parameter
564 | P13 Macro/User | P13.09 | User-defined parameter
565 | P13 Macro/User | P13.10 | User-defined parameter
566 | P13 Macro/User | P13.11 | User-defined parameter
567 | P13 Macro/User | P13.12 | User-defined parameter
568 | P13 Macro/User | P13.13 | User-defined parameter
569 | P13 Macro/User | P13.14 | User-defined parameter
570 | P13 Macro/User | P13.15 | User-defined parameter
571 | P13 Macro/User | P13.16 | User-defined parameter
572 | P13 Macro/User | P13.17 | User-defined parameter
573 | P13 Macro/User | P13.18 | User-defined parameter
574 | P13 Macro/User | P13.19 | User-defined parameter
575 | P13 Macro/User | P13.20 | User-defined parameter
576 | P13 Macro/User | P13.21 | User-defined parameter
577 | P13 Macro/User | P13.22 | User-defined parameter
578 | P13 Macro/User | P13.23 | User-defined parameter
579 | P13 Macro/User | P13.24 | User-defined parameter
580 | P13 Macro/User | P13.25 | User-defined parameter
581 | P13 Macro/User | P13.26 | User-defined parameter
582 | P13 Macro/User | P13.27 | User-defined parameter
583 | P13 Macro/User | P13.28 | User-defined parameter
584 | P13 Macro/User | P13.29 | User-defined parameter
585 | P13 Macro/User | P13.30 | User-defined parameter
586 | P13 Macro/User | P13.31 | User-defined parameter
587 | P13 Macro/User | P13.32 | User-defined parameter
588 | P13 Macro/User | P13.33 | User-defined parameter
589 | P13 Macro/User | P13.34 | User-defined parameter
590 | P13 Macro/User | P13.35 | User-defined parameter
591 | P13 Macro/User | P13.36 | User-defined parameter
592 | P13 Macro/User | P13.37 | User-defined parameter
593 | P13 Macro/User | P13.38 | User-defined parameter
594 | P13 Macro/User | P13.39 | User-defined parameter
595 | P13 Macro/User | P13.40 | User-defined parameter
596 | P13 Macro/User | P13.41 | User-defined parameter
597 | P13 Macro/User | P13.42 | User-defined parameter
598 | P13 Macro/User | P13.43 | User-defined parameter
599 | P13 Macro/User | P13.44 | User-defined parameter
600 | P13 Macro/User | P13.45 | User-defined parameter
601 | P13 Macro/User | P13.46 | User-defined parameter
602 | P13 Macro/User | P13.47 | User-defined parameter
603 | P13 Macro/User | P13.48 | User-defined parameter
604 | P13 Macro/User | P13.49 | User-defined parameter
605 | P13 Macro/User | P13.50 | User-defined parameter
606 | P14 Protection(2) | P14.50 | Output frequency at malfunction 2 | 0.00-599.00 Hz |  | Read | 0
607 | P14 Protection(2) | P14.51 | DC bus voltage at malfunction 2 | 0.0-6553.5 V |  | Read | 0
608 | P14 Protection(2) | P14.52 | Output current at malfunction 2 | 0.00-655.35 Amp |  | Read | 0
609 | P14 Protection(2) | P14.53 | IGBT temperature at malfunction 2 | -3276.7-3276.70C |  | Read | 0
610 | P14 Protection(2) | P14.54 | Output frequency at malfunction 3 | 0.00-599.00 Hz |  | Read | 0
611 | P14 Protection(2) | P14.55 | DC bus voltage at malfunction 3 | 0.0-6553.5 V |  | Read | 0
612 | P14 Protection(2) | P14.56 | Output current at malfunction 3 | 0.00-655.35 Amp |  | Read | 0
613 | P14 Protection(2) | P14.57 | IGBT temperature at malfunction 3 | -3276.7-3276.70C |  | Read | 0
614 | P14 Protection(2) | P14.58 | Output frequency at malfunction 4 | 0.00-599.00 Hz |  | Read | 0
615 | P14 Protection(2) | P14.59 | DC bus voltage at malfunction 4 | 0.0-6553.5 V |  | Read | 0
616 | P14 Protection(2) | P14.60 | Output current at malfunction 4 | 0.00-655.35 Amp |  | Read | 0
617 | P14 Protection(2) | P14.61 | IGBT temperature at malfunction 4 | -3276.7-3276.70C |  | Read | 0
618 | P14 Protection(2) | P14.62 | Output frequency at malfunction 5 | 0.00-599.00 Hz |  | Read | 0
619 | P14 Protection(2) | P14.63 | DC bus voltage at malfunction 5 | 0.0-6553.5 V |  | Read | 0
620 | P14 Protection(2) | P14.64 | Output current at malfunction 5 | 0.00-655.35 Amp |  | Read | 0
621 | P14 Protection(2) | P14.65 | IGBT temperature at malfunction 5 | -3276.7-3276.70C |  | Read | 0
622 | P14 Protection(2) | P14.66 | Output frequency at malfunction 6 | 0.00-599.00 Hz |  | Read | 0
623 | P14 Protection(2) | P14.67 | DC bus voltage at malfunction 6 | 0.0-6553.5 V |  | Read | 0
624 | P14 Protection(2) | P14.68 | Output current at malfunction 6 | 0.00-655.35 Amp |  | Read | 0
625 | P14 Protection(2) | P14.69 | IGBT temperature at malfunction 6 | -3276.7-3276.70C |  | Read | 0
626 | P14 Protection(2) | P14.70 | Fault record 7 | Refer to fault record P06.17-P06.22 |  | ♦R/W | 0
627 | P14 Protection(2) | P14.71 | Fault record 8 | Refer to fault record P06.17-P06.22 |  | ♦R/W | 0
628 | P14 Protection(2) | P14.72 | Fault record 9 | Refer to fault record P06.17-P06.22 |  | ♦R/W | 0
629 | P14 Protection(2) | P14.73 | Fault record 10 | Refer to fault record P06.17-P06.22 |  | ♦R/W | 0
630 | P14 Protection(2) | P14.74 | Over-torque detection selection (motor 3) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN |  | ♦R/W | 0
631 | P14 Protection(2) | P14.75 | Over-torque detection level (motor 3) | 10-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 120
632 | P14 Protection(2) | P14.76 | Over-torque detection time (motor 3) | 0.1-60.0 sec. |  | ♦R/W | 0.1
633 | P14 Protection(2) | P14.77 | Over-torque detection selection (motor 4) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN |  | ♦R/W | 0
634 | P14 Protection(2) | P14.78 | Over-torque detection level (motor 4) | 10-250% (100% corresponds the rated current of the drive) |  | ♦R/W | 120
635 | P14 Protection(2) | P14.79 | Over-torque detection time (motor 4) | 0.1-60.0 sec. |  | ♦R/W | 0.1
636 | P14 Protection(2) | P14.80 | Electronic thermal relay selection 3 (motor 3) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with the fan on the shaft) 2: Disable |  | ♦R/W | 2
637 | P14 Protection(2) | P14.81 | Electronic thermal relay action time 3 (motor 3) | 30.0-600.0 sec. |  | ♦R/W | 60
638 | P14 Protection(2) | P14.82 | Electronic thermal relay selection 4 (motor 4) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with the fan on the shaft) 2: Disable |  | ♦R/W | 2
639 | P14 Protection(2) | P14.83 | Electronic thermal relay action time 4 (motor 4) | 30.0-600.0 sec. |  | ♦R/W | 60

## REV
Revision history
Version | Description | Description
V1.0 | Release to webstore | 2020-07-22